## Cover
EU Code of Conduct for Data Centres Data Collection form |  | v15.1 | 2024 | Additional
Instructions
Data centre operators need to internally track energy consumption to improve efficiency. It is also valuable for the Code of Conduct to track its impact. Therefore, where possible this should be reported following the guidelines as closely as possible. In line with best practice, where this is not practical, a short explanation should be provided and alternatives assessed. |  |  |  | FAQ
This sheet is protected to help operators complete the correct sections using the password "CoC"
When completing the form, | green are expected
data elements in: | white are optional
Note that practices are | Entire data centre
highlighted in four colours | New IT equipment
New software
Build or refit 2016 onwards
New Applicants: | Follow links in blue
New applicants should enter expected information on each sheet where practical, Column O should be information that supports the implementation or adoption of the best practice, Column P should be an explanation as to why the best practice cannot be implemented, if this is the case then an entry should be made in Column Q (this will then form part of your action plan), finally endorsement actions are required for all best practices (Column R) There must be an entry in either Column O, OR Column P, If there is an entry in Column P, there must be an entry in Column Q. All applicants must fill complete Column R. Please note that failure to provide an entry in the required columns will result in a rejection of your application.
3 months energy consumption data should also be reported (following links in purple below)
This is used to characterise your data centre(s)
Energy reporting/Action Plan Progress | Follow links in orange
Enter 12 months (one month for applicants) energy consumption for DC and IT.
Provide an update on action plan (if applicable)
Please note that failure to update energy data or action plan (if applicable for the following year after approval will result in removal from the participant register.
Please submit completed forms to:
paolo.bertoldi@ec.europa.eu
All data will be collected by the EC and treated confidentially
Only anonymised data is reported as detailed in the Data Confidentiality Guidelines

## Instructions
Home
Code of Conduct for Data Centres Energy Efficiency
Reporting Form
Data Collection Guidelines
§ If data elements change over time (e.g. the number of racks, UPS utilization), provide the average of that element over the 12 month data collection period.
§ If you have any specific questions about the items listed below, or difficulty assessing data during this data collection period, please send an email to paolo.bertoldi@ec.europa.eu.
Data Elements List
The following table outlines the data elements of interest; each section of the table corresponds to a tab in this MS Excel Data Template.
Data Element Name | Description/Question
Best Practices
Practice | For each practice, please enter whether it has been implemented or if not the planned implementation due date. Additional comments can also be added. These could be reasons the practice cannot be implemented or is inappropriate in this data centre. Forms that fail to have an entry in at least one of either "comments", "reasons why the practice cannot be implemented", "action plan" or "endorsing actions" WILL be rejected. These will be used to assess the application for participant status as well as for correlation of the best practices with actual measured efficiency
Data Centre Information
Data Center Name or ID | Please provide a unique name (or number) for each data center in your sample.
Location | Please provide nearest city (to help us determine the DC climate zone)
Type of Data Center | Please select among the following: 1 = Traditional Enterprise; 2 = On-Demand Enterprise; 3 = Telecom; 4 = High Performance Computing Center (Scientific); 5 = Hosting; 6 = Internet; 7 = Hybrid
Type of Building | Please select between the following: 1 = Stand-alone, 2 = Enclosed in a larger building (i.e. office building or other space type). NOTE: If the data center is enclosed within another building space, it must be completely submetered in order to proceed with this data collection.
Building Floor Area | Provide the gross or total floor area of the building. Gross floor area is useful to give an idea of the proportion of floor space a data centre might occupy, particularly if enclosed in a larger building.
Data Center Floor Area | Provide the floor area of the data center space that includes the rack equipment, service clearance and circulation, control console area, power distribution, and local air conditioning that is encapsulated by the proper protective walls. Exclude administrative offices, storage, loading docks, and other non-essential space that does not directly support the operation of the data center.
Year Constructed | Enter the year of the most recent major commissioning of the data centre space. The building itself could be significantly older.
For any element that may change over the course of the data collection period (e.g. number of racks, UPS utilization), please provide an average figure for the 12 months of data.
Basic Role of Operator | Choose which of the roles best describes your organisation's activities in the data centre. This is useful for assessment of applications
Domain of Control | Choose, for each identified aspect of the data centre (physical building to business process) whether your organisation (including any parent, subsidiary or group organisation) has; Control, Partial Control or No Control over this aspect. This allows the application form to identify which of the best practices your organisation should be Implementing or Endorsing.
Electrical Infrastructure Resilience Level | Modern best practice recommends building facilities with more than one available electrical infrastructure resilience level in place of monolithic resilience levels. Identify which of the stated resilience levels N, N+1, 2N (including 2N+1) are available to IT equipment installed in this data centre.
Cooling Infrastructure Resilience Level | Modern best practice recommends building facilities with more than one available cooling infrastructure resilience level in place of monolithic resilience levels. Identify which of the stated resilience levels N, N+1, 2N (including 2N+1) are available to IT equipment installed in this data centre.
Number of modular capacity steps or separately provisioned halls | If your data centre was provisioned (power and cooling capacity delivered in modular steps of capacity) how many stages of capacity or separately delivered halls (/ zones) did / does the modular build allow for?
Number of Racks | Please provide the number of physical racks in the data center that are typically in operation.
Installed IT power | Please enter sum of the nominal power demand, in kW, of the network equipment, servers and storage equipment installed in the data centre computer room floor area;
Rated IT electrical Load in kW | Enter the as-provisioned peak power that can be provided to the IT equipment (or raised floor) in kW (may need further clarification)
Air temperature set points | Please enter the upper and lower temperature set points in degrees celsius
Humidity set points | Please enter humidity set points as configured in percentage RH or dew point (or both e.g. 15C and 60%RH)
Percentage of Average IT Utilization | What is the current "average" IT processing load as a percentage of the total server processor capacity? Enter this percentage as one average calculation for the entire year.
Percentage of Peak IT Utilization | What is the current "peak" IT processing load as a percentage of the total server processor capacity? Enter this percentage as one average calculation for the entire year.
Mechanical System Type | Please select the type of mechanical system used for cooling the data center: 1 = Direct Expansion; 2 = Chilled Water; 3 = Condenser; 4 = Other
IT Measurement
Total IT Plug Energy from UPS Meter in kWh | Please enter the annual total IT plug energy, as measured in kWh, from the output of a UPS meter, for energy going into the computer room (not crac units, etc.). This can be entered as one value for the year or as a series of meter/energy readings (i.e. monthly or periodic) that cover the entire calendar year. It is preferable that these measurements are read at approximately the same period and frequency as the utility meter for the building.
Start Date | For each energy use value, enter a start and end date. You can provide an entry for each meter/energy reading or one entry for the entire year.
End Date
Total IT Plug Energy from PDU Meter in kWh (If Available) | Please enter the annual total IT plug energy, as measured in kWh, from the input of a PDU meter, for energy going into the computer room (not crac units, etc.). This can be entered as one value for the year or as a series of meter/energy readings (i.e. monthly or periodic) that cover the entire calendar year. It is preferrable that these measurements are read at approximately the same period and frequency as the utility meter for the building. If both the UPS and PDU meters are provided, an estimate of the difference between the total UPS and the sum of the PDU's will be estimated as the non-critical UPS load that might be serving the office, mechanical and non-data center loads.
Start Date | For each energy use value, enter a start and end date. You can provide an entry for each meter/energy reading or one entry for the entire year.
End Date
Electricity Data
Provide the annual electricity consumption for the building (if a stand-alone data center) or the submetered data center. You can provide this as one value for the year or as a series of meter/energy bill entries that cover the entire year.
Meter ID | Enter a distinguishing name or number for each meter.
Start Date | For each energy use value, enter a start and end date. You can provide an entry for each bill or one entry for the entire year.
End Date
Electricity Consumption in kWh | Enter the electricity consumption in kWh corresponding to the start and end date.

## FAQs
Home
Frequently Asked Questions (FAQ)
Review the additional information for select questions below. If you need further clarification, email your questions to: paolo.bertoldi@ec.europa.eu
Data Centre Information
Type of Data Center
1 - Traditional Enterprise: Processes data requirements for data center owner 2 - On Demand Enterprise: Processes and expands data processing capacity, when needed, for numerous customers (this would include batch processing and manufacturing type data processing facilities) 3 - Telecom: Telecom Switching Center 4 - High Performance Computing: Scientific and high density data processing 5 - Hosting: Sells data processing services to numerous Customers 6 - Internet: Provides high capacity processing for large numbers of web clients 7 - Hybrid: Combination of two or more of the above
Percentage of Average IT Utilization
The processor, network and storage processes that occur in the data center are frequently automatically monitored and reported as part of the IT management. Both average and peak loads are frequently captured for capacity planning and other purposes. The average estimate over time of the IT equipment’s utilization is a value that currently will not affect the index but is the first step in data capture that will allow correlation the actual IT processing work with efficiency. It is understood that different devices will be measured by different criteria for example, servers by processor, network by throughput, storage by capacity or performance. Although there is not yet a standard metric to measure IT work being processed with energy input, this one measurement of the equipment activity verses a dormant state will provide an estimation of the potential for energy saving features, if activated, that could achieve even better efficiencies.
Percentage of Peak IT Utilization
The processor, network and storage processes that occur in the data center are frequently automatically monitored and reported as part of the IT management. Both average and peak loads are frequently captured for capacity planning and other purposes. The collection purpose for peak load is to provide an understanding of the maximum equipment necessary for peak periods and then, depending on the variability of the enterprise processing needs, dormant during the non-peak times. It is understood that different devices will be measured by different criteria for example, servers by processor, network by throughput, storage by capacity or performance. By understanding the peak and average utilization characteristics of the data center, analysis with the tracking of input energy and the extent of dormant equipment sitting in reserve for the peak. If these processes are tracked for the data center, the use of devices that can slow down processor clock speed and turn off redundant processors can then be estimated. These concepts are the start of understanding IT work efficiency. For where the data is captured, ask your console operator or check the measurement in the IT utility program available in the processor equipment.
IT Measurement
Total IT Plug Energy
In general the calculation is attempting to capture the energy used by the IT equipment (this will include the IT equipment fan systems and all other devices: KVM, cabinet monitoring and cabinet circulation fans) that are connected into the plug strip serving the computer room. If the UPS system is only providing load to the computer equipment in the data center, and NOT providing Computer room fans, pumps, telecommunication closets and desktop services outside the data center, then the UPS readings – over time can be recorded. The best case in this circumstance is to read a kWh meter at approximately the same period and frequency as the utility meter for the building. If a kWh meter is not available on the UPS then the instantaneous meter reading can be measured on a periodic basis to predict how load on the UPS changes with the data center processing load. A comparison with the known processing peak and the lowest utilization would be good times to record instantaneous meter readings to capture the range of UPS output. If it is greater than 5%, a more detailed (greater frequency) of recording would be used to estimate the total kWh provided by the UPS over time.

## Data Centre Information
< Prev | 1/2 Next > | Home
Data Centre Information
Building Information
Data Center Name / ID |  | Example #1
Location
Type of Data Center |  | 1 - Traditional Enterprise
Type of Building |  | 1 - Stand-Alone
Building floor area |  | Example #M
Data Center floor area |  | Example #M
Year Constructed |  | Example 1999
Type of Operator
Basic type of operator |  | Operator
If other please specify
Operator Domain of Control
Physical Building |  | Y | Select Y/N
Mechanical & Electrical Plant |  | Y | Select Y/N
Data Floor |  | Y | Select Y/N
Racks |  | Y | Select Y/N
IT Equipment |  | Y | Select Y/N
Operating System / Virtualisation Layer |  | Y | Select Y/N
Software |  | Y | Select Y/N
Business Process |  | Y | Select Y/N
Full Control |  | Y
Operation |  | Resilience Level In Use?
Electrical Infrastructure Resilience Level | N | No | Select Yes / No
| N+1 | No | Select Yes / No
| 2N | No | Select Yes / No
Cooling Infrastructure Resilience Level | N | No | Select Yes / No
| N+1 | No | Select Yes / No
| 2N | No | Select Yes / No
Number of modular capacity steps or separately provisioned halls
Number of Racks
Installed IT power (kW) |  |  | Optional
Rated IT electrical load
Target IT equipment intake temperature
CRAC / AHU Air temp upper (and lower) set point(s)
Air temperature control method |  | Return
Humidity upper and lower set points
% of Average IT Utilization |  |  | Optional
% of Peak IT Utilization |  |  | Optional
Economiser Type |  | 0 = None
Mechanical System Type |  | 1 = Direct Expansion
Note on A5: Please provide a unique name or number for each data center. Make sure to use the same identifier on each tab!
Note on A6: Please provide nearest city
Note on A7: Please select one of the seven types of data centers.
Note on A8: Please select one of the two building types.
Note on A9: Please provide the square metres of floor area of the entire building in which the data centre is housed
Note on A10: Please provide the square metres of the data center space, including all space that directly supports the operation of the data center
Note on A14: Liam Newcombe: Select the role that best describes your activity in this data centre.
Note on A16: Liam Newcombe: Identify for each listed aspect of the data centre whether your organisation (including any parent, subsidiary or group company) has N - No control over this aspect Partial - Some control but not full over this aspect (e.g. a colo operator has partial control over racks where customers rent suites and install their own) Y - Control over this aspect
Note on A17: Liam Newcombe: The building including security, location and maintenance
Note on A18: Liam Newcombe: The selection, installation, configuration, maintenance and management of the mechanical and electrical plant
Note on A19: Liam Newcombe: The installation, configuration, maintenance and management of the main data floor where IT equipment is installed. This includes the floor (raised in some cases), positioning of CRAC units and PDUs, basic layout of cabling systems (under floor or overhead).
Note on A20: Liam Newcombe: The installation, configuration, maintenance and management of the racks into which rack mount IT equipment is installed
Note on A21: Liam Newcombe: The selection, installation, configuration, maintenance and management of the physical IT equipment.
Note on A22: Liam Newcombe: The selection, installation, configuration, maintenance and management of the Operating System and virtualisation (both client and hypervisor) software installed on the IT equipment. This includes monitoring clients, hardware management agents etc.
Note on A23: Liam Newcombe: The selection, installation, configuration, maintenance and management of the application software installed on the IT equipment.
Note on A24: Liam Newcombe: The determination and communication of the business requirements for the data centre including the importance of systems, reliability availability and maintainability specifications and data management processes.
Note on A25: Liam Newcombe: This cell is automatically calculated
Note on A28: Select which levels of infrastructure resilience are available to IT equipment, this may be multiple levels in a modular or multiple resilience level facility.
Note on A35: Liam Newcombe: If your data centre was provisioned (power and cooling capacity delivered in modular steps of capacity) how many stages of capacity or separately delivered halls (/ zones) did / does the modular build allow for?
Note on A36: Provide the number of physical racks that are usually in operation.
Note on A37: Thi is the sum of the nominal power demand, in kW, of the network equipment, servers and storage equipment installed in the data centre computer room floor area;
Note on A38: This is the as-provisioned peak power that can be provided to the IT equipment (or raised floor) in kW, not the average power being provided to the IT equipment.
Note on A39: This is the target temperature for air entering the IT equipment, not the supply or return set point on the air conditioning equipment.
Note on A40: Enter upper and lower temperature set points for the data floor CRAC or AHU in degrees C
Note on A41: Do the air temperature set points above apply to the air supplied from the CRAC / AHU to the IT equipment or the return air from the IT equipment to the CRAC / AHU?
Note on A42: Enter upper and lower Humidity set points as percentage RH and / or dew point
Note on A45: If the cooling system is fitted with an economiser which type of economiser is fitted? The types of economiser are described in section 5.4 of the best practice documentation

## Data Centre KPIs
< Prev | 1/2 Next > | Home
Data Centre KPIs
Metric | Acceptable Method | Result | Category (if applicable) | end of measurement period (DD/MM/YYYY)
Power Utilisation Effectiveness (PUE) | ISO/IEC 30134-2 or EN 50600-4-2
Renewable Energy Factor | ISO/IEC 30134-3 or EN 50600-4-3
IT Energy Efficiency (Server) (ITEEsv) | ISO/IEC 30134-4
IT Equipment Utilisation (ITEUsv) | ISO/IEC 30134-5
Energy Reuse Factor (ERF) | ISO/IEC 30134-6 or EN 50600-4-6
Cooling Effciiency Ratio (CER) | ISO/IEC 30134-7 or EN 50600-4-7
Carbon Utilisation Efficiency (CUE) | ISO/IE 30134-8 or EN 50600-4-8
Water Utilisation Effectiveness (WUE) | ISO/IEC 30134-9 or EN 50600-4-9
Water Utilisation Effectiveness Source(WUEs) | ISO/IEC 30134-9 or EN 50600-4-9

## Best Practices
< Prev | 2/2 Best Practice Reporting | Home | Next>
Identify the Best Practices Implemented or Endorsed for this data centre.
Application Date:
| Missing Practices: | 98 | [60 empty] | Guidance to operators with partial control of the data centre
|  |  |  | Enter the status of the practice in this data centre | [5 empty] | Expected Status based on responsibility areas | [7 empty] | Committed Status |  |  | Implemented Status |  |  |  |  | Endorsed Status | [5 empty] | These cells are used to determine the practice status column | [12 empty] | Controlled | [8 empty] | Not Controlled | [5 empty] | Resulting Action |  | These cells provide suggestions and guidance on how the applicant should Implement of Endorse practices if they have only partial control of the data centre.
|  |  |  | Complete either due date or status for each practice | [5 empty] | These cells provide guidance
Number | Practice | Value | Practice Status | Commit to Implement Date | Commit to Endorse Date | Entire Data Centre | New IT Equipment | New Software | New Build or Retrofit | Entire Data Centre | New IT Equipment | New Software | New Build or Retrofit | Applicant comments or further description | Reason why this practice cannot be implemented in this data centre | Action Plan | Endorsing Actions Taken | Commit to Implement status | Commit to Endorse status | Overall Committed | Entire Estate | New IT Equipment | New Software | Data Centre Refit | Overall Implemented | Entire Estate | New IT Equipment | New Software | Data Centre Refit | Overall Endorsed | Overall Endorsed not Implemented | Entire Estate | New IT Equipment | New Software | Data Centre Refit | Entire Estate | New IT Equipment | New Software | Data Centre Refit | Overall Missing | Physical Building | Mechanical & Electrical Plant | Data Floor | Racks | IT Equipment | Operating System / Virtualisation Layer | Software | Business Process | Full Control | Physical Building | Mechanical & Electrical Plant | Data Floor | Racks | IT Equipment | Operating System / Virtualisation Layer | Software | Business Process | Full Control | Implement? | Endorse? | Action | CoLo | CoLo Customer | IT Service Provider | Services Customer
Data Centre Utilisation, Management and Planning
Involvement of Organisational Groups
3.1.1 | Group involvement | 5 | N | [6 empty] | I | [9 empty] | 0 | N |  |  |  | 0 |  |  |  |  | 0 | 0 | Y |  |  |  | 1 | 0 | 0 | 0 | 1 | I | I | I | I | I | I | I | I | I | [8 empty] | E | I |  | I | Consider endorsing by inviting major customers onto the approval board. The approval board should set the standards for equipment and installation that customers need to comply with. | At least software and hardware should be covered. Major customers should invite their CoLo suppliers onto this board or attend the CoLo operator's approval board if the operator is a Participant | Consider endorsing by inviting major customers onto the approval board. The approval board should set the standards for equipment and installation that customers need to comply with where they select equipment | At least one member of the entity procuring services should engage with the service provider's approval board to ensure that the impacts of decisions on both sides are fully understood.
General Policies
3.2.1 | Consider the embedded energy in devices | 3 | N | [6 empty] | I | [9 empty] | 0 | N |  |  |  | 0 |  |  |  |  | 0 | 0 | Y |  |  |  | 1 | 0 | 0 | 0 | 1 |  | I |  |  | I | [5 empty] | E |  |  | E |  |  |  |  | I |  | I | This would only apply to M&E plant | This would only apply to IT devices | IT devices and M&E plant | This would apply to the impact on IT devices of service or software changes.
3.2.2 | Mechanical and electrical equipment environmental operating ranges | 4 | N | [9 empty] | I | [6 empty] | 0 |  |  |  | N | 0 |  |  |  |  | 0 | 0 |  |  |  | Y | 0 | 0 | 0 | 1 | 1 |  | I | [8 empty] | E | [6 empty] | E | I |  | I |  |  |  | This is a joint matter between the procurer and supplier and will vary with the contract type. The key point of note here is that the legacy approach of 'no single point of failure' and 'dual everything' fails to consider the basic reality of reliability and maintainability and produces over-complex solutions which cannot be operated reliably or at reasonable cost.
3.2.3 | Service Charging Models | 3 | [17 empty] | 0 |  |  |  |  | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | [24 empty] | This is a joint matter between the procurer and supplier and will vary with the contract type. The key point of note here is that the legacy approach of 'no single point of failure' and 'dual everything' fails to consider the basic reality of reliability and maintainability and produces over-complex solutions which cannot be operated reliably or at reasonable cost.
3.2.4 | Life Cycle Assessment | 3 | N | [9 empty] | I | [6 empty] | 0 |  |  |  | N | 0 |  |  |  |  | 0 | 0 |  |  |  | Y | 0 | 0 | 0 | 1 | 1 | I | I | I | I | I | I | I | I | I | [8 empty] | E | I |  | I |  |  |  | This is a joint matter between the procurer and supplier and will vary with the contract type. The key point of note here is that the legacy approach of 'no single point of failure' and 'dual everything' fails to consider the basic reality of reliability and maintainability and produces over-complex solutions which cannot be operated reliably or at reasonable cost.
3.2.5 | Environmental Management | 3 | N | [6 empty] | I | [9 empty] | 0 | N |  |  |  | 0 |  |  |  |  | 0 | 0 | Y |  |  |  | 1 | 0 | 0 | 0 | 1 | I | I | I | I | I | I | I | I | I | [8 empty] | E | I |  | I
3.2.6 | Energy Management | 3 | N | [6 empty] | I | [9 empty] | 0 | N |  |  |  | 0 |  |  |  |  | 0 | 0 | Y |  |  |  | 1 | 0 | 0 | 0 | 1 | I | I | I | I | I | I | I | I | I | [8 empty] | E | I |  | I
3.2.7 | Asset Management | 3 | N | [6 empty] | I | [9 empty] | 0 | N |  |  |  | 0 |  |  |  |  | 0 | 0 | Y |  |  |  | 1 | 0 | 0 | 0 | 1 | I | I | I | I | I | I | I | I | I | [8 empty] | E | I |  | I
3.2.8 | Sustainable energy usage | 3 | N | [6 empty] | I | [9 empty] | 0 | N |  |  |  | 0 |  |  |  |  | 0 | 0 | Y |  |  |  | 1 | 0 | 0 | 0 | 1 | I | I | I | I | I | I | I | I | I | [8 empty] | E | I |  | I
3.2.9 | Powering of devices via the IT cabling | 1 | [17 empty] | 0 |  |  |  |  | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | [24 empty] | This is a joint matter between the procurer and supplier and will vary with the contract type. The key point of note here is that the legacy approach of 'no single point of failure' and 'dual everything' fails to consider the basic reality of reliability and maintainability and produces over-complex solutions which cannot be operated reliably or at reasonable cost.
3.2.10 | Impact of mobile / shifting workloads | 2 | [17 empty] | 0 |  |  |  |  | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | [24 empty] | This is a joint matter between the procurer and supplier and will vary with the contract type. The key point of note here is that the legacy approach of 'no single point of failure' and 'dual everything' fails to consider the basic reality of reliability and maintainability and produces over-complex solutions which cannot be operated reliably or at reasonable cost.
3.2.11 | Alternative power generation technologies | 1 | [17 empty] | 0 |  |  |  |  | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | [24 empty] | This is a joint matter between the procurer and supplier and will vary with the contract type. The key point of note here is that the legacy approach of 'no single point of failure' and 'dual everything' fails to consider the basic reality of reliability and maintainability and produces over-complex solutions which cannot be operated reliably or at reasonable cost.
3.2.12 | Monitor and manage air quality | 2 | N | [6 empty] | I | [9 empty] | 0 | N |  |  |  | 0 |  |  |  |  | 0 | 0 | Y |  |  |  | 1 | 0 | 0 | 0 | 1 | I | I | I | I | I | I | I | I | I | [8 empty] | E | I |  | I
3.2.13 | Consider technical areas of data centres as industrial space | 3 | N | [6 empty] | I | [9 empty] | 0 | N |  |  |  | 0 |  |  |  |  | 0 | 0 | Y |  |  |  | 1 | 0 | 0 | 0 | 1 |  | I | [8 empty] | E | [7 empty] | I |  | I
3.2.14 | Site Documentation | 3 | N | [6 empty] | I | [9 empty] | 0 | N |  |  |  | 0 |  |  |  |  | 0 | 0 | Y |  |  |  | 1 | 0 | 0 | 0 | 1 |  | I | [8 empty] | E | [7 empty] | I |  | I
3.2.15 | Training & Development | 3 | N | [6 empty] | I | [9 empty] | 0 | N |  |  |  | 0 |  |  |  |  | 0 | 0 | Y |  |  |  | 1 | 0 | 0 | 0 | 1 |  | I | [8 empty] | E | [7 empty] | I |  | I
3.2.16 | Smart Grid | 2
Resilience Level and Provisioning
3.3.1 | Build resilience to business requirements | 3 | N | [9 empty] | I | [6 empty] | 0 |  |  |  | N | 0 |  |  |  |  | 0 | 0 |  |  |  | Y | 0 | 0 | 0 | 1 | 1 |  | I | [5 empty] | I |  |  | E | [7 empty] | I |  | I | This may be achieved through either or both of multiple facilities of different resilience levels or multiple levels of resilience in the same facility dependent upon customer demand type. This solution can be scale dependent. | The service customer entity should audit and describe their requirements for RAMS based on actual requirements and impacts. This should then be mapped through the IT hardware and the correct levels of data centre infrastructure resilience requested per platform or application and the appropriate levels of facility resilience selected. | This may be achieved through either or both of multiple facilities of different resilience levels or multiple levels of resilience in the same facility dependent upon customer demand type. This solution can be scale dependent. | The service customer entity should audit and describe their requirements for RAMS based on actual requirements and impacts, rather than requiring a single 99.9XX% target for all services requiring the supplier to install and operate unecessary duplicate equipment and supporting infrastructure due to a failure to understand, describe and prioritise services.
3.3.2 | Consider multiple levels of resilience | 3 | N | [9 empty] | I | [6 empty] | 0 |  |  |  | N | 0 |  |  |  |  | 0 | 0 |  |  |  | Y | 0 | 0 | 0 | 1 | 1 |  | I |  |  | I |  |  | I |  |  | E | [6 empty] | E | I |  | I | This may be achieved through either or both of multiple facilities of different resilience levels or multiple levels of resilience in the same facility dependent upon customer demand type. The choice of approach may be scale dependent. Operators should communicate the cost and energy benefits of different resilience levels to customers. | The service customer entity should audit and describe their requirements for RAMS based on actual requirements and impacts. This should then be mapped through the IT hardware and the correct levels of data centre infrastructure resilience requested per platform or application. | Service providers should be able to map differing customer requested levels of service availability onto mechanical and electrical infrastructure reliability. This may be achieved through either multiple facilities of different resilience levels or multiple levels of resilience in the same facility. Operators should communicate the cost and energy benefits of different resilience levels to customers. | The service customer entity should audit and describe their requirements for RAMS based on actual requirements and impacts, and preferentially select providers able to meet these varied levels of resilience.
3.3.3 | Lean provisioning of power and cooling for a maximum of 18 months of data floor capacity | 3 | N | [9 empty] | I | [6 empty] | 0 |  |  |  | N | 0 |  |  |  |  | 0 | 0 |  |  |  | Y | 0 | 0 | 0 | 1 | 1 |  | I |  |  | I | [5 empty] | E |  |  | E |  |  |  |  | I |  | I | "Reserved" capacity which is unused should not be considered as used for the purpose of this assessment. Colo operators should dissuade customers from reserving excessive capacity. | Colo customers should never reserve more than 18 months worth of live capacity in an operating facility | "Reserved" capacity which is unused should not be considered as used for the purpose of this assessment.
3.3.4 | Design infrastructure to maximise part load efficiency | 3 | N | [9 empty] | I | [6 empty] | 0 |  |  |  | N | 0 |  |  |  |  | 0 | 0 |  |  |  | Y | 0 | 0 | 0 | 1 | 1 |  | I | [8 empty] | E | [7 empty] | I |  | I
3.3.5 | Design appropriate levels of resilience | 4 | [17 empty] | 0 |  |  |  |  | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | [24 empty] | This is a joint matter between the procurer and supplier and will vary with the contract type. The key point of note here is that the legacy approach of 'no single point of failure' and 'dual everything' fails to consider the basic reality of reliability and maintainability and produces over-complex solutions which cannot be operated reliably or at reasonable cost.
IT Equipment and Services
Selection and Deployment of New IT Equipment
4.1.1 | IT hardware – Power | 5 | N | [7 empty] | I | [8 empty] | 0 |  | N |  |  | 0 |  |  |  |  | 0 | 0 |  | Y |  |  | 0 | 1 | 0 | 0 | 1 |  |  |  |  | I | [8 empty] | E |  |  |  |  | I |  | I | Colo providers should endorse to customers the cost and energy benefits of more energy efficienct hardware. Operators may wish to offer services to assist customers in selecting hardware that will function efficiently in the target data centre. | Colo customers should select efficient IT hardware and also consider working with their Colo provider to ensure that the equipment is suitable for the target facility. | Service provders should select efficienct hardware, in addition service provider should endorse to customers the cost and energy benefits of more energy efficienct hardware where customers are involved in purchasing and selection. Operators may wish to offer services to assist customers in selecting hardware that will function efficiently in the target data centre. | Services customers should select energy efficient hardware where they have influence over hardware selection.
4.1.2 | New IT hardware – Restricted (legacy) operating temperature and humidity range | 4 | N | [7 empty] | I | [8 empty] | 0 |  | N |  |  | 0 |  |  |  |  | 0 | 0 |  | Y |  |  | 0 | 1 | 0 | 0 | 1 |  |  |  |  | I | [8 empty] | E |  |  |  |  | I |  | I | Colo providers should clearly communicate to customers that the operating temperature and humidity ranges of equipment are a key cost factor and what the targets for the facility are. Consider a surcharge for dealing with equipment which has restrictive requirements. | Colo customers should procure equipment with as wide an operating range as possible. | Service providers should specify the minimum operating temperature and humidity ranges for their data centre to customers where the customer selects IT equipment. | Customers should obtain the standard operating range information for temperature and humidity from their service provider before procuring equipment.
4.1.3 | New IT hardware – Expected operating temperature and humidity range | 5 | N | [7 empty] | I | [8 empty] | 0 |  | N |  |  | 0 |  |  |  |  | 0 | 0 |  | Y |  |  | 0 | 1 | 0 | 0 | 1 |  |  |  |  | I | [8 empty] | E |  |  |  |  | I |  | I | Colo providers should clearly communicate to customers that the operating temperature and humidity ranges of equipment are a key cost factor and what the targets for the facility are. Consider a surcharge for dealing with equipment which has restrictive requirements. | Colo customers should procure equipment with as wide an operating range as possible. | Service providers should specify the minimum operating temperature and humidity ranges for their data centre to customers where the customer selects IT equipment. | Customers should obtain the standard operating range information for temperature and humidity from their service provider before procuring equipment.
4.1.4 | New IT hardware – Extended operating temperature and humidity range | 3 | [17 empty] | 0 |  |  |  |  | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0
4.1.5 | Select IT equipment suitable for the data centre power density and cooling delivery capabilities. | 3 | N | [7 empty] | I | [8 empty] | 0 |  | N |  |  | 0 |  |  |  |  | 0 | 0 |  | Y |  |  | 0 | 1 | 0 | 0 | 1 |  |  |  |  | I | [8 empty] | E |  |  |  |  | I |  | I | Colo providers should clearly communicate the power density and cooling design standard for the data centre to customers. | Colo customers should be fully aware of the data centre power density limits and cooling design standards | Service providers should clearly communicate the power density and cooling design standard for the data centre to customers. | Services customers should be fully aware of the data centre power density limits and cooling design standards
4.1.6 | IT equipment power usage against inlet temperature | 5 | N | [7 empty] | I | [8 empty] | 0 |  | N |  |  | 0 |  |  |  |  | 0 | 0 |  | Y |  |  | 0 | 1 | 0 | 0 | 1 |  |  |  |  | I | [8 empty] | E |  |  |  |  | I |  | I
4.1.7 | Select equipment suitable for the data centre - Air flow direction | 4 | N | [7 empty] | I | [8 empty] | 0 |  | N |  |  | 0 |  |  |  |  | 0 | 0 |  | Y |  |  | 0 | 1 | 0 | 0 | 1 |  |  |  |  | I | [8 empty] | E |  |  |  |  | I |  | I
4.1.8 | Enable power management features | 5 | N | [7 empty] | I | [8 empty] | 0 |  | N |  |  | 0 |  |  |  |  | 0 | 0 |  | Y |  |  | 0 | 1 | 0 | 0 | 1 |  |  |  |  | I | I | [7 empty] | E | E |  |  |  | I |  | I |  |  |  | Customers should not obstruct providers using power management except in the rare cases of applications whose latency profile or code does not allow power management. Both dynamic power and sleep modes should be evaluated.
4.1.9 | Provision to the actual IT power usage based on components installed | 3 | N | [7 empty] | I | [8 empty] | 0 |  | N |  |  | 0 |  |  |  |  | 0 | 0 |  | Y |  |  | 0 | 1 | 0 | 0 | 1 |  | I |  |  | I | [8 empty] | E |  |  |  |  | I |  | I | Colo providers should ensure that customers understand that they should provision to the peak and not the nameplate power. It may be appropriate to offer services to assist the customer in tracking provisioned power.
4.1.10 | EU ECO Design/Energy Star compliant hardware | 4 | N | [7 empty] | I | [8 empty] | 0 |  | N |  |  | 0 |  |  |  |  | 0 | 0 |  | Y |  |  | 0 | 1 | 0 | 0 | 1 |  | I |  |  | I | [8 empty] | E |  |  |  |  | I |  | I | Colo providers should ensure that customers understand that they should provision to the peak and not the nameplate power. It may be appropriate to offer services to assist the customer in tracking provisioned power.
4.1.11 | Energy & temperature reporting hardware | 3 | N | [7 empty] | I | [8 empty] | 0 |  | N |  |  | 0 |  |  |  |  | 0 | 0 |  | Y |  |  | 0 | 1 | 0 | 0 | 1 |  | I |  |  | I | [8 empty] | E |  |  |  |  | I |  | I | Colo providers should ensure that customers understand that they should provision to the peak and not the nameplate power. It may be appropriate to offer services to assist the customer in tracking provisioned power.
4.1.12 | Control of equipment energy use | 5 | [17 empty] | 0 |  |  |  |  | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0
4.1.13 | When forced to use select free standing equipment suitable for the data centre – Airflow direction | 4 | N | [7 empty] | I | [8 empty] | 0 |  | N |  |  | 0 |  |  |  |  | 0 | 0 |  | Y |  |  | 0 | 1 | 0 | 0 | 1 |  |  |  |  | I | [8 empty] | E |  |  |  |  | I |  | I | Colo providers should clearly communicate the standard air flow direction for the data centre to customers in addition to any restrictions that air containment systems may place on cabinets or housings. |  | Service providers should clearly communicate the standard air flow direction for the data centre to customers where they select equipment.
4.1.14 | Operating temperature range – Liquid cooled IT equipment | 4 | [17 empty] | 0 |  |  |  |  | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0
4.1.15 | AC/DC Converter efficiency | 3 | N | [7 empty] | I | [8 empty] | 0 |  | N |  |  | 0 |  |  |  |  | 0 | 0 |  | Y |  |  | 0 | 1 | 0 | 0 | 1 |  |  |  |  | I | [8 empty] | E |  |  |  |  | I |  | I
Deployment of New IT Services
4.2.1 | Deploy using Virtualisation technologies | 5 | N | [7 empty] | I | [8 empty] | 0 |  | N |  |  | 0 |  |  |  |  | 0 | 0 |  | Y |  |  | 0 | 1 | 0 | 0 | 1 | [5 empty] | I | [8 empty] | E |  |  |  | I |  | I |  |  | Service providers should implement this practice and actively endorse the cost and energy benefits to customers. | Service customers should require this practice as part of their procurement process. Service customers should not obstruct service providers in implementing resource sharing platforms.
4.2.2 | Reduce IT hardware resilience level | 4 | N | [7 empty] | I | [8 empty] | 0 |  | N |  |  | 0 |  |  |  |  | 0 | 0 |  | Y |  |  | 0 | 1 | 0 | 0 | 1 |  |  |  |  | I | [8 empty] | E |  |  |  |  | I |  | I |  |  | Service providers should implement this practice and actively endorse the cost and energy benefits to customers. | Service customers should require this practice as part of their procurement process. Service customers actively engage with their providers to determine the required level of hardware resilience from the real service incident impact information for each service.
4.2.3 | Reduce Hot / Cold standby equipment | 4 | N | [7 empty] | I | [8 empty] | 0 |  | N |  |  | 0 |  |  |  |  | 0 | 0 |  | Y |  |  | 0 | 1 | 0 | 0 | 1 |  |  |  |  | I | [8 empty] | E |  |  |  |  | I |  | I |  |  | Service providers should implement this practice and actively endorse the cost and energy benefits to customers. | Service customers should require this practice as part of their procurement process. Service customers actively engage with their providers to determine the required level of hardware resilience from the real service incident impact information for each service.
4.2.4 | Select efficient software | 5 | N | [8 empty] | I | [7 empty] | 0 |  |  | N |  | 0 |  |  |  |  | 0 | 0 |  |  | Y |  | 0 | 0 | 1 | 0 | 1 | [5 empty] | I | I | [7 empty] | E | E |  |  | I |  | I |  |  | Service providers should implement this practice and actively endorse the cost and energy benefits to customers. | Service customers should require this practice as part of their procurement process. Service customers should actively engage with their service providers where they influence software selection to map real requirements through software and optimise cost and energy.
4.2.5 | Develop efficient software | 5 | N | [8 empty] | I | [7 empty] | 0 |  |  | N |  | 0 |  |  |  |  | 0 | 0 |  |  | Y |  | 0 | 0 | 1 | 0 | 1 | [6 empty] | I | [8 empty] | E |  |  | I |  | I |  |  | Service providers should implement this practice and actively endorse the cost and energy benefits to customers. | Service customers should require this practice as part of their procurement process. Service customers should actively engage with their service providers where they develop custom software for the provider to operate to optimise the energy and operational cost of the software
4.2.6 | Incentives to develop efficient software | 5 | [17 empty] | 0 |  |  |  |  | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0
4.2.7 | Eliminate traditional 2N hardware clusters | 4 | [17 empty] | 0 |  |  |  |  | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0
4.2.8 | IT Equipment utilisation | 4 | [17 empty] | 0 |  |  |  |  | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0
4.2.9 | Network Energy Use | 2 | [17 empty] | 0 |  |  |  |  | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0
Management of Existing IT Equipment and Services
4.3.1 | Audit existing physical and service estate | 5 | N | [6 empty] | I | [9 empty] | 0 | N |  |  |  | 0 |  |  |  |  | 0 | 0 | Y |  |  |  | 1 | 0 | 0 | 0 | 1 |  |  |  |  | I | I | I | I | [5 empty] | E | E | E | E |  | I |  | I |  |  |  | Customers should actively engage with their service providers to determine when services are unused and support their decommissioning.
4.3.2 | Decommission and remove unused equipment | 5 | N | [6 empty] | I | [9 empty] | 0 | N |  |  |  | 0 |  |  |  |  | 0 | 0 | Y |  |  |  | 1 | 0 | 0 | 0 | 1 |  |  |  |  | I | I | I | I | [5 empty] | E | E | E | E |  | I |  | I |  |  |  | Customers should actively engage with their service providers to determine when services are unused and support their decommissioning.
4.3.3 | Virtualise and archive legacy services | 5 | [17 empty] | 0 |  |  |  |  | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | [13 empty] | E | E | E | E
4.3.4 | Consolidation of existing services | 5 | N | [6 empty] | I | [9 empty] | 0 | N |  |  |  | 0 |  |  |  |  | 0 | 0 | Y |  |  |  | 1 | 0 | 0 | 0 | 1 |  |  |  |  | I | I | I | I | [5 empty] | E | E | E | E |  | I |  | I
4.3.5 | Decommission low business value services | 4 | N | [6 empty] | I | [9 empty] | 0 | N |  |  |  | 0 |  |  |  |  | 0 | 0 | Y |  |  |  | 1 | 0 | 0 | 0 | 1 |  |  |  |  | I | I | I | I | [5 empty] | E | E | E | E |  | I |  | I
4.3.6 | Shut down and consider removal of idle equipment. | 4 | N | [6 empty] | I | [9 empty] | 0 | N |  |  |  | 0 |  |  |  |  | 0 | 0 | Y |  |  |  | 1 | 0 | 0 | 0 | 1 |  |  |  |  | I | I | I | I | [5 empty] | E | E | E | E |  | I |  | I
4.3.7 | Control of system energy use | 4 | [17 empty] | 0 |  |  |  |  | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0
4.3.8 | Audit of existing IT environmental requirements | 4 | N | [6 empty] | I | [9 empty] | 0 | N |  |  |  | 0 |  |  |  |  | 0 | 0 | Y |  |  |  | 1 | 0 | 0 | 0 | 1 |  |  |  |  | I | I | I | I | [5 empty] | E | E | E | E |  | I |  | I | Colo providers should provide zones or areas where equipment identified under this best practice can be moved (refer to BP 5.1.10 & 5.1.12) | Colo customers should request that providers provide zones or areas under BP's 5.1.10 & 5.1.12 | Service providers should create zones or areas where customers can place equipment with tighter environmental controls | Customers should actively engage with their service providers to identify and move equipment into zones or areas with tighter environmental controls
Data Management
4.4.1 | Data Management Policy | 3 | N | [6 empty] | I | [9 empty] | 0 | N |  |  |  | 0 |  |  |  |  | 0 | 0 | Y |  |  |  | 1 | 0 | 0 | 0 | 1 | [7 empty] | I | [8 empty] | E |  | I |  | I |  |  | Implement for data controlled by the provider. Actively endorse to customers and provide multiple levels of data retention / protection. | This applies to the procuring entity. There is little the outsource provider can do without categorised data and policies.
4.4.2 | Separate user logical data storage areas by retention and protection policy | 3 | [17 empty] | 0 |  |  |  |  | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0
4.4.3 | Separate physical data storage areas by protection and performance requirements | 4 | [17 empty] | 0 |  |  |  |  | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0
4.4.4 | Select lower power storage devices | 4 | [17 empty] | 0 |  |  |  |  | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0
4.4.5 | Reduce total data volume | 4 | [17 empty] | 0 |  |  |  |  | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0
4.4.6 | Reduce total storage volume | 4 | [17 empty] | 0 |  |  |  |  | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0
Cooling
Air Flow Management and Design
5.1.1 | Design – Hot / Cold aisle | 5 | N | [7 empty] | I |  | I | [6 empty] | 0 |  | N |  | N | 0 |  |  |  |  | 0 | 0 |  | Y |  | Y | 0 | 1 | 0 | 1 | 1 |  |  | I | I | [7 empty] | E | E | [5 empty] | I |  | I | This applies to Colo operators, a number of operators have already put in place programs to convert existing populated Colo facilities to hot / cold aisle including customer information programs. | The colo customer is equally responsible for hot / cold layout and should both endorse to their colo provider and assist the provider in achieving hot / cold aisle through correct installation of new equipment. |  | Service customers should require this practice as part of their procurement process.
5.1.2 | Design – Contained hot or cold air | 5 | N | [9 empty] | I | [6 empty] | 0 |  |  |  | N | 0 |  |  |  |  | 0 | 0 |  |  |  | Y | 0 | 0 | 0 | 1 | 1 |  |  | I | I | [7 empty] | E | E | [5 empty] | I |  | I | This applies to Colo operators, a number of Colo data centres have already implemented full containment without loss of customers. | The customer should both endorse this to their colo providers by selecting facilities with full containment over non contained facilities and also procure and install equipment in such a way as to support containment. This includes selecting equipment with appropriate airflow directions that fits in standard racks etc. |  | Service customers should preferentially select providers using contained hot / cold air flow data centres.
5.1.3 | Design – Contained hot or cold air – Retrofit | 4 | N | [9 empty] | I | [6 empty] | 0 |  |  |  | N | 0 |  |  |  |  | 0 | 0 |  |  |  | Y | 0 | 0 | 0 | 1 | 1 |  |  | I | I | [7 empty] | E | E | [5 empty] | I |  | I
5.1.4 | Rack air flow management – Blanking Plates | 3 | N | [6 empty] | I | [9 empty] | 0 | N |  |  |  | 0 |  |  |  |  | 0 | 0 | Y |  |  |  | 1 | 0 | 0 | 0 | 1 |  |  |  | I | [8 empty] | E | [5 empty] | I |  | I | This applies to Colo operators, a number of Colo data centres have already implemented full blanking and received positive customer feedback | The customer should a) endorse this to their colo providers by assisting in retrofit or maintenance of blanking b) procure and install equipment in such a way as to support blanking c) Select colo providers that have implemented or have a committed implementation date for blanking |  | Service customers should require this practice as part of their procurement process.
5.1.5 | Rack air flow management – Other Openings | 3 | N | [9 empty] | I | [6 empty] | 0 |  |  |  | N | 0 |  |  |  |  | 0 | 0 |  |  |  | Y | 0 | 0 | 0 | 1 | 1 |  |  |  | I | [8 empty] | E | [5 empty] | I |  | I | This applies to Colo operators, a number of Colo data centres have already implemented full blanking and received positive customer feedback | The customer should a) endorse this to their colo providers by assisting in retrofit or maintenance of air flow management b) procure and install equipment in such a way as to support air flow management c) select providers who have implemented or have a committed date for this practice |  | Service customers should require this practice as part of their procurement process.
5.1.6 | Provide adequate free area on rack doors | 4 | N | [7 empty] | I |  | I | [6 empty] | 0 |  | N |  | N | 0 |  |  |  |  | 0 | 0 |  | Y |  | Y | 0 | 1 | 0 | 1 | 1 |  |  |  | I | [8 empty] | E | [5 empty] | I |  | I | Colo providers should comply with this for racks that they supply and inform customers of the requirement and spec for any customer supplied racks | A colo customer should review the racks provided by their colo provider and ensure that any customer racks that they install meet these requirements. |  | Service customers should require this practice as part of their procurement process.
5.1.7 | Raised floor air flow management | 3 | N | [6 empty] | I | [9 empty] | 0 | N |  |  |  | 0 |  |  |  |  | 0 | 0 | Y |  |  |  | 1 | 0 | 0 | 0 | 1 |  |  | I | [8 empty] | E | [6 empty] | I |  | I |  |  |  | Service customers should require this practice as part of their procurement process.
5.1.8 | Raised floor air flow management – obstructions | 3 | N | [6 empty] | I | [9 empty] | 0 | N |  |  |  | 0 |  |  |  |  | 0 | 0 | Y |  |  |  | 1 | 0 | 0 | 0 | 1 |  |  | I | [8 empty] | E | [6 empty] | I |  | I |  |  |  | Service customers should require this practice as part of their procurement process.
5.1.9 | Design – Return plenums | 3 | [17 empty] | 0 |  |  |  |  | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0
5.1.10 | Design – Raised floor or suspended ceiling height | 3 | [17 empty] | 0 |  |  |  |  | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0
5.1.11 | Equipment segregation | 3 | N | [7 empty] | I |  | I | [6 empty] | 0 |  | N |  | N | 0 |  |  |  |  | 0 | 0 |  | Y |  | Y | 0 | 1 | 0 | 1 | 1 |  |  | I | I | [7 empty] | E | E | [5 empty] | I |  | I | This applies to Colo operators, a number of operators have already put in place programs to convert existing populated Colo facilities to hot / cold aisle including customer information programs. | The colo customer is equally responsible for hot / cold layout and should both endorse to their colo provider and assist the provider in achieving hot / cold aisle through correct installation of new equipment. |  | Service customers should require this practice as part of their procurement process.
5.1.12 | Control of supplied air flow volume minimizing over pressure | 3 | N | [9 empty] | I | [6 empty] | 0 |  |  |  | N | 0 |  |  |  |  | 0 | 0 |  |  |  | Y | 0 | 0 | 0 | 1 | 1 |  |  |  | I | [8 empty] | E | [5 empty] | I |  | I | Colo providers should comply with this for racks that they supply and inform customers of the requirement and spec for any customer supplied racks | A colo customer should review the racks provided by their colo provider and ensure that any customer racks that they install meet these requirements. |  | Service customers should require this practice as part of their procurement process.
Cooling Management
5.2.1 | Scalable or modular installation and use of cooling equipment | 3 | [17 empty] | 0 |  |  |  |  | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0
5.2.2 | Shut down unnecessary cooling equipment | 4 | N | [6 empty] | I | [9 empty] | 0 | N |  |  |  | 0 |  |  |  |  | 0 | 0 | Y |  |  |  | 1 | 0 | 0 | 0 | 1 |  | I | I | I | I | [5 empty] | E | E | E | E |  |  |  |  | I |  | I
5.2.3 | Review of cooling before IT equipment changes | 4 | N | [6 empty] | I | [9 empty] | 0 | N |  |  |  | 0 |  |  |  |  | 0 | 0 | Y |  |  |  | 1 | 0 | 0 | 0 | 1 |  | I | I | I | I | [5 empty] | E | E | E | E |  |  |  |  | I |  | I | Colo providers should assist customers in reviewing and optimising cooling as part of change control whenever a customer removes or adds IT equipment. | Colo customers should both request that their colo provider assist in cooling review prior to changes and actively engage their change management processes with the colo provider. |  | Service customers should require this practice as part of their procurement process.
5.2.4 | Review of cooling strategy | 4 | N | [6 empty] | I | [9 empty] | 0 | N |  |  |  | 0 |  |  |  |  | 0 | 0 | Y |  |  |  | 1 | 0 | 0 | 0 | 1 |  | I | I | I | I | [5 empty] | E | E | E | E |  |  |  |  | I |  | I | Colo providers should carry out this review and also notify customers of the review output where it impacts the customer or where the customer has actions that could improve cooling. | Colo customers should request that their colo provider performs this periodic review and supplies a report. Customers should also actively engage with their Colo provider to assist in implementing the opportunities identified in the review |  | Service customers should require this practice as part of their procurement process.
5.2.5 | Review CRAC / AHU Settings | 4 | N | [6 empty] | I | [9 empty] | 0 | N |  |  |  | 0 |  |  |  |  | 0 | 0 | Y |  |  |  | 1 | 0 | 0 | 0 | 1 |  | I | I | I | I | [5 empty] | E | E | E | E |  |  |  |  | I |  | I
5.2.6 | Dynamic control of building cooling | 3 | [17 empty] | 0 |  |  |  |  | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0
5.2.7 | Effective regular maintenance of Cooling Plant | 2 | N | [6 empty] | I | [9 empty] | 0 | N |  |  |  | 0 |  |  |  |  | 0 | 0 | Y |  |  |  | 1 | 0 | 0 | 0 | 1 |  | I | I | I | I | [5 empty] | E | E | E | E |  |  |  |  | I |  | I | Colo providers should carry out this review and also notify customers of the review output where it impacts the customer or where the customer has actions that could improve cooling. | Colo customers should request that their colo provider performs this periodic review and supplies a report. Customers should also actively engage with their Colo provider to assist in implementing the opportunities identified in the review |  | Service customers should require this practice as part of their procurement process.
5.2.8 | Review and if possible optimise chilled water temperature | 4 | N | [6 empty] | I | [9 empty] | 0 | N |  |  |  | 0 |  |  |  |  | 0 | 0 | Y |  |  |  | 1 | 0 | 0 | 0 | 1 |  | I | [8 empty] | E | [7 empty] | I |  | I
Temperature and Humidity Settings
5.3.1 | Review and if possible raise target IT equipment intake air temperature | 4 | N | [6 empty] | I | [9 empty] | 0 | N |  |  |  | 0 |  |  |  |  | 0 | 0 | Y |  |  |  | 1 | 0 | 0 | 0 | 1 |  | I |  |  | I | [5 empty] | E |  |  | E |  |  |  |  | I |  | I | Colo providers should run their facilities at the upper end of the current ASHRAE range. Colo providers should actively recommend to customers the benefits of increased temperature settings. | Colo customers should not obstruct their colo provider by refusing to agree to increased target temperatures (e.g. 23-25C). Colo customers should select colo providers based on their ability to run at higer set points. |  | Service customers include the set temperatures for the data floor as part of their procurement assessment process.
5.3.2 | Review and widen the working humidity range | 4 | N | [6 empty] | I | [9 empty] | 0 | N |  |  |  | 0 |  |  |  |  | 0 | 0 | Y |  |  |  | 1 | 0 | 0 | 0 | 1 |  | I |  |  | I | [5 empty] | E |  |  | E |  |  |  |  | I |  | I | Colo providers should set as wide a range of humidity as can be supported and actively recommend to customers the benefits of increased humidity range. | Colo customers should not obstruct their colo provider by refusing to agree to increased humidity control ranges. Colo customers should select colo providers based on the breadth of their working range. |  | Service customers should include the set humidity range for the data floor as part of their procurement process.
5.3.3 | Expanded IT equipment inlet environmental conditions (temperature and humidity) | 5 | [17 empty] | 0 |  |  |  |  | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0
5.3.4 | Separate environmental zones | 4 | N | [9 empty] | I | [6 empty] | 0 |  |  |  | N | 0 |  |  |  |  | 0 | 0 |  |  |  | Y | 0 | 0 | 0 | 1 | 1 |  |  |  | I | [8 empty] | E | [5 empty] | I |  | I | Colo providers should comply with this for racks that they supply and inform customers of the requirement and spec for any customer supplied racks | A colo customer should review the racks provided by their colo provider and ensure that any customer racks that they install meet these requirements. |  | Service customers should require this practice as part of their procurement process.
5.3.5 | Separate environmental zones – Colocation or Managed Service Provider | 4 | N | [9 empty] | I | [6 empty] | 0 |  |  |  | N | 0 |  |  |  |  | 0 | 0 |  |  |  | Y | 0 | 0 | 0 | 1 | 1 |  |  |  | I | [8 empty] | E | [5 empty] | I |  | I | Colo providers should comply with this for racks that they supply and inform customers of the requirement and spec for any customer supplied racks | A colo customer should review the racks provided by their colo provider and ensure that any customer racks that they install meet these requirements. |  | Service customers should require this practice as part of their procurement process.
Free and Economised Cooling
5.4.1.1 | Direct air free cooling | 5 | [17 empty] | 0 |  |  |  |  | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0
5.4.1.2 | Indirect air free cooling | 5 | [17 empty] | 0 |  |  |  |  | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0
5.4.1.3 | Indirect water free cooling with CRAH and dry cooler or cooling tower | 5 | [17 empty] | 0 |  |  |  |  | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | [24 empty] | This is a joint matter between the procurer and supplier and will vary with the contract type. The key point of note here is that the legacy approach of 'no single point of failure' and 'dual everything' fails to consider the basic reality of reliability and maintainability and produces over-complex solutions which cannot be operated reliably or at reasonable cost.
5.4.1.4 | Indirect water free cooling with CRAC with integrated free cooling coil. | 4 | [17 empty] | 0 |  |  |  |  | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | [24 empty] | This is a joint matter between the procurer and supplier and will vary with the contract type. The key point of note here is that the legacy approach of 'no single point of failure' and 'dual everything' fails to consider the basic reality of reliability and maintainability and produces over-complex solutions which cannot be operated reliably or at reasonable cost.
5.4.1.5 | Indirect water free cooling with CRAH and free cooling chiller. | 3 | [17 empty] | 0 |  |  |  |  | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | [24 empty] | This is a joint matter between the procurer and supplier and will vary with the contract type. The key point of note here is that the legacy approach of 'no single point of failure' and 'dual everything' fails to consider the basic reality of reliability and maintainability and produces over-complex solutions which cannot be operated reliably or at reasonable cost.
5.4.1.6 | Indirect water free cooling with condenser water cooling chilled water | 3 | [17 empty] | 0 |  |  |  |  | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | [24 empty] | This is a joint matter between the procurer and supplier and will vary with the contract type. The key point of note here is that the legacy approach of 'no single point of failure' and 'dual everything' fails to consider the basic reality of reliability and maintainability and produces over-complex solutions which cannot be operated reliably or at reasonable cost.
5.4.1.7 | Alternative cooling sources | 1 | [17 empty] | 0 |  |  |  |  | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | [24 empty] | This is a joint matter between the procurer and supplier and will vary with the contract type. The key point of note here is that the legacy approach of 'no single point of failure' and 'dual everything' fails to consider the basic reality of reliability and maintainability and produces over-complex solutions which cannot be operated reliably or at reasonable cost.
5.4.1.8 | Free Cooling installation | 5 | N | [9 empty] | I | [6 empty] | 0 |  |  |  | N | 0 |  |  |  |  | 0 | 0 |  |  |  | Y | 0 | 0 | 0 | 1 | 1 |  | I | [8 empty] | E | [7 empty] | I |  | I
Cooling Plant
5.4.2.1 | Chillers with high COP (EER) | 3 | N | [9 empty] | I | [6 empty] | 0 |  |  |  | N | 0 |  |  |  |  | 0 | 0 |  |  |  | Y | 0 | 0 | 0 | 1 | 1 |  | I | [8 empty] | E | [7 empty] | I |  | I
5.4.2.2 | Cooling system operating temperatures | 3 | N | [6 empty] | I | [9 empty] | 0 | N |  |  |  | 0 |  |  |  |  | 0 | 0 | Y |  |  |  | 1 | 0 | 0 | 0 | 1 |  | I | [8 empty] | E | [7 empty] | I |  | I
5.4.2.3 | Efficient part load operation | 3 | N | [9 empty] | I | [6 empty] | 0 |  |  |  | N | 0 |  |  |  |  | 0 | 0 |  |  |  | Y | 0 | 0 | 0 | 1 | 1 |  | I | [8 empty] | E | [7 empty] | I |  | I
5.4.2.4 | Variable speed drives for compressors, pumps and fans | 4 | N | [9 empty] | I | [6 empty] | 0 |  |  |  | N | 0 |  |  |  |  | 0 | 0 |  |  |  | Y | 0 | 0 | 0 | 1 | 1 |  | I | [8 empty] | E | [7 empty] | I |  | I
5.4.2.5 | Select systems which facilitate the use of “Free Cooling” | 5 | N | [9 empty] | I | [6 empty] | 0 |  |  |  | N | 0 |  |  |  |  | 0 | 0 |  |  |  | Y | 0 | 0 | 0 | 1 | 1 |  | I | [8 empty] | E | [7 empty] | I |  | I
5.4.2.6 | Do not share data centre chilled water system with comfort cooling | 4 | N | [9 empty] | I | [6 empty] | 0 |  |  |  | N | 0 |  |  |  |  | 0 | 0 |  |  |  | Y | 0 | 0 | 0 | 1 | 1 |  | I | [8 empty] | E | [7 empty] | I |  | I
5.4.2.7 | Do not allow non IT equipment to dictate cooling system set-points | 4 | N | [9 empty] | I | [6 empty] | 0 |  |  |  | N | 0 |  |  |  |  | 0 | 0 |  |  |  | Y | 0 | 0 | 0 | 1 | 1 |  | I | [8 empty] | E | [7 empty] | I |  | I
5.4.2.8 | Chilled water pump control strategy | 4 | N | [9 empty] | I | [6 empty] | 0 |  |  |  | N | 0 |  |  |  |  | 0 | 0 |  |  |  | Y | 0 | 0 | 0 | 1 | 1 |  | I | [8 empty] | E | [7 empty] | I |  | I
4
Computer Room Air Conditioners | [19 empty] | 0 |  |  |  |  | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0
5.5.1 | Variable Speed Fans | 4 | N | [9 empty] | I | [6 empty] | 0 |  |  |  | N | 0 |  |  |  |  | 0 | 0 |  |  |  | Y | 0 | 0 | 0 | 1 | 1 |  | I | [8 empty] | E | [7 empty] | I |  | I
5.5.2 | Control on CRAC / CRAH unit supply air temperature. | 3 | N | [9 empty] | I | [6 empty] | 0 |  |  |  | N | 0 |  |  |  |  | 0 | 0 |  |  |  | Y | 0 | 0 | 0 | 1 | 1 |  | I | [8 empty] | E | [7 empty] | I |  | I
5.5.3 | Run variable speed CRAC/CRAH units in parallel | 4 | [17 empty] | 0 |  |  |  |  | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0
5.5.4 | Sequencing of CRAC/CRAH units | 2 | [17 empty] | 0 |  |  |  |  | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0
5.5.5 | Do not control humidity at CRAC/CRAH unit | 4 | N | [9 empty] | I | [6 empty] | 0 |  |  |  | N | 0 |  |  |  |  | 0 | 0 |  |  |  | Y | 0 | 0 | 0 | 1 | 1 |  | I | [8 empty] | E | [7 empty] | I |  | I
5.5.6 | Cooling unit sizing and selection | 4 | N | [9 empty] | I | [6 empty] | 0 |  |  |  | N | 0 |  |  |  |  | 0 | 0 |  |  |  | Y | 0 | 0 | 0 | 1 | 1 |  | I | [8 empty] | E | [7 empty] | I |  | I
Direct Liquid Cooling
5.6.1 | Direct liquid cooling of IT devices | 4 | [17 empty] | 0 |  |  |  |  | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0
Reuse of Data Centre Waste Heat | [19 empty] | 0
5.7.1 | Waste heat re-use | 4 | N | [9 empty] | I | [6 empty] | 0 |  |  |  | N | 0 |  |  |  |  | 0 | 0 |  |  |  | Y | 0 | 0 | 0 | 1 | 1 | I | [7 empty] | I | E | [8 empty] | I |  | I
5.7.2 | Heat pump assisted waste heat re-use | 4 | N | [9 empty] | I | [6 empty] | 0 |  |  |  | N | 0 |  |  |  |  | 0 | 0 |  |  |  | Y | 0 | 0 | 0 | 1 | 1 | I | [7 empty] | I | E | [8 empty] | I |  | I
5.7.3 | Use data floor waste heat to warm generator and fuel storage areas | 2 | [17 empty] | 0 |  |  |  |  | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0
5.7.4 | Energy reuse metrics and reporting | 1 | [17 empty] | 0 |  |  |  |  | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0
5.7.5 | Capture Ready Infrastructure | 1 | [17 empty] | 0 |  |  |  |  | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0
Data Centre Power Equipment
Selection and Deployment of New Power Equipment | [19 empty] | 0 |  |  |  |  | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0
6.1.1 | Modular UPS Deployment | 3 | N | [9 empty] | I | [6 empty] | 0 |  |  |  | N | 0 |  |  |  |  | 0 | 0 |  |  |  | Y | 0 | 0 | 0 | 1 | 1 |  | I | [8 empty] | E | [7 empty] | I |  | I
6.1.2 | High efficiency UPS | 3 | N | [9 empty] | I | [6 empty] | 0 |  |  |  | N | 0 |  |  |  |  | 0 | 0 |  |  |  | Y | 0 | 0 | 0 | 1 | 1 |  | I | [8 empty] | E | [7 empty] | I |  | I
6.1.3 | Use efficient UPS operating modes | 2 | N | [9 empty] | I | [6 empty] | 0 |  |  |  | N | 0 |  |  |  |  | 0 | 0 |  |  |  | Y | 0 | 0 | 0 | 1 | 1 |  | I | [8 empty] | E | [7 empty] | I |  | I | Colo providers should endorse the benefits of more efficient UPS operating modes to customers.
6.1.4 | Elimination of Isolation Transformers | 3 | N | [9 empty] | I | [6 empty] | 0 |  |  |  | N | 0 |  |  |  |  | 0 | 0 |  |  |  | Y | 0 | 0 | 0 | 1 | 1 |  | I | [8 empty] | E | [7 empty] | I |  | I | Colo providers should endorse the benefits of more efficient UPS operating modes to customers.
6.1.6 | Efficient part load operation | 3 | N | [9 empty] | I | [6 empty] | 0 |  |  |  | N | 0 |  |  |  |  | 0 | 0 |  |  |  | Y | 0 | 0 | 0 | 1 | 1 |  | I | [8 empty] | E | [7 empty] | I |  | I | Colo providers should endorse the benefits of more efficient UPS operating modes to customers.
Management of Existing Power Equipment
6.2.1 | Reduce Engine-generator heater temperature set-point | 2 | [17 empty] | 0 |  |  |  |  | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0
6.2.2 | Power Factor Correction | 2 | [17 empty] | 0 |  |  |  |  | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | [24 empty] | This is a joint matter between the procurer and supplier and will vary with the contract type. The key point of note here is that the legacy approach of 'no single point of failure' and 'dual everything' fails to consider the basic reality of reliability and maintainability and produces over-complex solutions which cannot be operated reliably or at reasonable cost.
Other Data Centre Equipment | [19 empty] | 0 |  |  |  |  | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0
Office and Storage Spaces | [19 empty] | 0 |  |  |  |  | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0
7.1.1 | Turn off Lights | 1 | N | [6 empty] | I | [9 empty] | 0 | N |  |  |  | 0 |  |  |  |  | 0 | 0 | Y |  |  |  | 1 | 0 | 0 | 0 | 1 | I | [8 empty] | E | [8 empty] | I |  | I
7.1.2 | Low energy lighting | 1 | N | [9 empty] | I | [6 empty] | 0 |  |  |  | N | 0 |  |  |  |  | 0 | 0 |  |  |  | Y | 0 | 0 | 0 | 1 | 1 | I | [8 empty] | E | [8 empty] | I |  | I
71.3 | Pale coloured fixtures and fittings | 1 | N | [9 empty] | I | [6 empty] | 0 |  |  |  | N | 0 |  |  |  |  | 0 | 0 |  |  |  | Y | 0 | 0 | 0 | 1 | 1 | I | [8 empty] | E | [8 empty] | I |  | I
7.1.4 | Energy & temperature reporting hardware. | 3 | N | [9 empty] | I | [6 empty] | 0 |  |  |  | N | 0 |  |  |  |  | 0 | 0 |  |  |  | Y | 0 | 0 | 0 | 1 | 1 | I | [8 empty] | E | [8 empty] | I |  | I
Data Centre Building
Building Physical Layout
8.1.1 | Locate M&E plant outside the cooled area | 2 | N | [9 empty] | I | [6 empty] | 0 |  |  |  | N | 0 |  |  |  |  | 0 | 0 |  |  |  | Y | 0 | 0 | 0 | 1 | 1 | I | [8 empty] | E | [8 empty] | I |  | I
8.1.2 | Select or create a building with sufficient ‘slab to slab’ separation/ceiling height. | 3 | N | [9 empty] | I | [6 empty] | 0 |  |  |  | N | 0 |  |  |  |  | 0 | 0 |  |  |  | Y | 0 | 0 | 0 | 1 | 1 | I | [8 empty] | E | [8 empty] | I |  | I
8.1.3 | Facilitate the use of “Free Cooling” | 3 | N | [9 empty] | I | [6 empty] | 0 |  |  |  | N | 0 |  |  |  |  | 0 | 0 |  |  |  | Y | 0 | 0 | 0 | 1 | 1 | I | [8 empty] | E | [8 empty] | I |  | I
8.1.4 | Location and orientation of plant equipment | 2 | N | [9 empty] | I | [6 empty] | 0 |  |  |  | N | 0 |  |  |  |  | 0 | 0 |  |  |  | Y | 0 | 0 | 0 | 1 | 1 | I | [8 empty] | E | [8 empty] | I |  | I
8.1.5 | Minimise direct solar heating | 2 | N | [9 empty] | I | [6 empty] | 0 |  |  |  | N | 0 |  |  |  |  | 0 | 0 |  |  |  | Y | 0 | 0 | 0 | 1 | 1 | I | [8 empty] | E | [8 empty] | I |  | I
Building Geographic Location
8.2.1 | Locate the Data Centre where waste heat can be reused | 4 | [17 empty] | 0 |  |  |  |  | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0
8.2.2 | Locate the Data Centre in an area of low ambient temperature | 4 | [17 empty] | 0 |  |  |  |  | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0
8.2.3 | Avoid locating the data centre in high ambient humidity areas | 1 | [17 empty] | 0 |  |  |  |  | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0
8.2.4 | Locate near a source of free cooling | 3 | [17 empty] | 0 |  |  |  |  | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0
8.2.5 | Colocate with power source | 3 | [17 empty] | 0 |  |  |  |  | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0
Water Sources
8.3.1 | Capture rain water | 1 | [17 empty] | 0 |  |  |  |  | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | [24 empty] | This is a joint matter between the procurer and supplier and will vary with the contract type. The key point of note here is that the legacy approach of 'no single point of failure' and 'dual everything' fails to consider the basic reality of reliability and maintainability and produces over-complex solutions which cannot be operated reliably or at reasonable cost.
8.3.2 | Other water sources | 2 | [17 empty] | 0 |  |  |  |  | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | [24 empty] | This is a joint matter between the procurer and supplier and will vary with the contract type. The key point of note here is that the legacy approach of 'no single point of failure' and 'dual everything' fails to consider the basic reality of reliability and maintainability and produces over-complex solutions which cannot be operated reliably or at reasonable cost.
8.3.3 | Metering of water consumption | 2 | [17 empty] | 0 |  |  |  |  | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | [24 empty] | This is a joint matter between the procurer and supplier and will vary with the contract type. The key point of note here is that the legacy approach of 'no single point of failure' and 'dual everything' fails to consider the basic reality of reliability and maintainability and produces over-complex solutions which cannot be operated reliably or at reasonable cost.
Monitoring
Energy Use and Environmental Measurement
9.1.1 | Incoming energy consumption meter | 4 | N | [6 empty] | I | [9 empty] | 0 | N |  |  |  | 0 |  |  |  |  | 0 | 0 | Y |  |  |  | 1 | 0 | 0 | 0 | 1 |  | I | [8 empty] | E | [7 empty] | I |  | I
9.1.2 | IT Energy consumption meter | 4 | N | [6 empty] | I | [9 empty] | 0 | N |  |  |  | 0 |  |  |  |  | 0 | 0 | Y |  |  |  | 1 | 0 | 0 | 0 | 1 |  | I |  |  | I | [13 empty] | I |  | I |  | Colo customers should be able to provide the total IT energy consumption of their equipment. |  | Service customers should request the total IT energy consumption of equipment dedicated to their services.
9.1.3 | Room level metering of air temperature and humidity | 2 | N | [6 empty] | I | [9 empty] | 0 | N |  |  |  | 0 |  |  |  |  | 0 | 0 | Y |  |  |  | 1 | 0 | 0 | 0 | 1 |  | I |  |  | I | [13 empty] | I |  | I |  | Colo customers should be able to provide the total IT energy consumption of their equipment. |  | Service customers should request the total IT energy consumption of equipment dedicated to their services.
9.1.4 | CRAC / AHU unit level metering of supply or return air temperature and humidity | 3 | N | [6 empty] | I | [9 empty] | 0 | N |  |  |  | 0 |  |  |  |  | 0 | 0 | Y |  |  |  | 1 | 0 | 0 | 0 | 1 |  | I |  |  | I | [13 empty] | I |  | I |  | Colo customers should be able to provide the total IT energy consumption of their equipment. |  | Service customers should request the total IT energy consumption of equipment dedicated to their services.
9.1.5 | Distribution board level metering of Mechanical and Electrical energy consumption. | 3 | N | [9 empty] | I | [6 empty] | 0 |  |  |  | N | 0 |  |  |  |  | 0 | 0 |  |  |  | Y | 0 | 0 | 0 | 1 | 1 | I | [8 empty] | E | [8 empty] | I |  | I
9.1.6 | Cabinet level metering of IT Energy consumption | 3 | [17 empty] | 0 |  |  |  |  | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0
9.1.7 | Row or Cabinet level metering of temperature and humidity | 2 | [17 empty] | 0 |  |  |  |  | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0
9.1.8 | IT Device level metering of temperature | 4 | [17 empty] | 0 |  |  |  |  | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0
9.1.9 | IT Device level metering of energy consumption | 4 | [17 empty] | 0 |  |  |  |  | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0
Energy Use and Environmental Collection and Logging | [19 empty] | 0 |  |  |  |  | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0
9.2.1 | Periodic manual readings | 3 | N | [6 empty] | I | [9 empty] | 0 | N |  |  |  | 0 |  |  |  |  | 0 | 0 | Y |  |  |  | 1 | 0 | 0 | 0 | 1 |  | I |  |  | I | [5 empty] | E |  |  | E |  |  |  |  | I |  | I
9.2.2 | Automated daily readings | 4 | N | [9 empty] | I | [6 empty] | 0 |  |  |  | N | 0 |  |  |  |  | 0 | 0 |  |  |  | Y | 0 | 0 | 0 | 1 | 1 |  | I |  |  | I | [5 empty] | E |  |  | E |  |  |  |  | I |  | I
9.2.3 | Automated hourly readings | 4 | [17 empty] | 0 |  |  |  |  | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0
9.2.4 | Achieved economised cooling hours – new build DC | 4 | N | [9 empty] | I | [6 empty] | 0 |  |  |  | N | 0 |  |  |  |  | 0 | 0 |  |  |  | Y | 0 | 0 | 0 | 1 | 1 | I | [8 empty] | E | [8 empty] | I |  | I
Energy Use and Environmental Reporting
9.3.1 | Written reporting | 4 | N | [6 empty] | I | [9 empty] | 0 | N |  |  |  | 0 |  |  |  |  | 0 | 0 | Y |  |  |  | 1 | 0 | 0 | 0 | 1 |  | I | [8 empty] | E | [7 empty] | I |  | I |  | Colo customers should request a report for the energy consumption of their equipment. |  | Service customers should request a report for the energy consumption of their equipment.
9.3.2 | Energy and environmental reporting console | 4 | [17 empty] | 0 |  |  |  |  | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0
9.3.3 | Integrated IT energy and environmental reporting console | 4 | [17 empty] | 0 |  |  |  |  | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0
9.3.4 | Achieved economised cooling hours – new build DC | 4 | Y | [5 empty] | I |  |  |  | I | [6 empty] | 0 |  |  |  | Y | 1 |  |  |  |  | 0 | 0 |  |  |  | Y | 0 | 0 | 0 | 0 | 0 | I | [8 empty] | E | [8 empty] | I |  | I
9.3.5 | PUE and Partial PUE Reporting | 4 | [33 empty] | 0 | 0 | 0 | 0 | 0
9.3.6 | REF Reporting | 4 | [33 empty] | 0 | 0 | 0 | 0 | 0
9.3.7 | ITEEsv Reporting | 4 | [33 empty] | 0 | 0 | 0 | 0 | 0
9.3.8 | ITEUsv Reporting | 4 | [33 empty] | 0 | 0 | 0 | 0 | 0
9.3.9 | ERF Reporting | 4
9.3.10 | CER Reporting | 4
9.3.11 | CUE Reporting | 4
9.3.12 | WUE Reporting | 4
IT Reporting
9.4.1 | Server Utilisation | 3 | [17 empty] | 0 |  |  |  |  | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0
9.4.2 | Network Utilisation | 3 | [17 empty] | 0 |  |  |  |  | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0
9.4.3 | Storage Utilisation | 3 | [17 empty] | 0 |  |  |  |  | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0
9.4.4 | Business relevant dashboard | 3 | [17 empty] | 0 |  |  |  |  | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | [24 empty] | This is a joint matter between the procurer and supplier and will vary with the contract type. The key point of note here is that the legacy approach of 'no single point of failure' and 'dual everything' fails to consider the basic reality of reliability and maintainability and produces over-complex solutions which cannot be operated reliably or at reasonable cost.
[20 empty] | 0 |  |  |  |  | 1 |  |  |  |  | 0 | 0 |  |  |  |  | 36 | 18 | 2 | 45 | 98
Note on D8: Liam Newcombe: This column reports "Y" for a practice that has been implemented or endorsed as identified in the "Expected Status based on responsibility areas" or whose due date is within 36 months of the application date.
Note on E8: Liam Newcombe: If the practice is not yet implemented but you are committing to implement the practice by a specified date then enter that date in this column. You should also check the application date above in C3
Note on F8: Liam Newcombe: If you have implemented the practice to apply to the entire data centre, existing and new IT and M&E then select Implemented in this column. If the specified action requires endorsement then select Endorsed in this column and describe in the "Endorsing Actions Taken" column. If you have split control and are expected to both Implement and Endorse this practice then select I&E. Selecting Implemented or Endorsed in this column is understood to mean that the practice is Implemented or Endorsed for New IT Equipment, New Software and Refit.
Note on G8: Liam Newcombe: If you have implemented the practice to apply to the entire data centre, existing and new IT and M&E then select Implemented in this column. If the specified action requires endorsement then select Endorsed in this column and describe in the "Endorsing Actions Taken" column. If you have split control and are expected to both Implement and Endorse this practice then select I&E. Selecting Implemented or Endorsed in this column is understood to mean that the practice is Implemented or Endorsed for New IT Equipment, New Software and Refit.
Note on H8: Liam Newcombe: If you have implemented the practice to apply only to new IT equipment in this data centre then select Implemented in this column. If the specified action requires endorsement then select Endorsed in this column and describe in the "Endorsing Actions Taken" column. If you have split control and are expected to both Implement and Endorse this practice then select I&E.
Note on I8: Liam Newcombe: If you have implemented the practice to apply only to new software in this data centre then select Implemented in this column. If the specified action requires endorsement then select Endorsed in this column and describe in the "Endorsing Actions Taken" column. If you have split control and are expected to both Implement and Endorse this practice then select I&E.
Note on J8: Liam Newcombe: These practices are expected for data centres which were constructed or underwent a major refit including removal of IT equipment from 2010 onwards. If your data centre was built or refitted after 2010 and have implemented the practice or you will implement this practice in any upgrade or retrofit of this data centre then select Implemented in this column. If the specified action requires endorsement then select Endorsed in this column and describe in the "Endorsing Actions Taken" column. If you have split control and are expected to both Implement and Endorse this practice then select I&E.
Note on K8: Liam Newcombe: This column identifies whether this expected practice should be Implemented, Endorsed or both Implemented and Endorsed based upon the areas of control selected on the "Data Centre Information" tab.
Note on L8: Liam Newcombe: This column identifies whether this expected practice should be Implemented, Endorsed or both Implemented and Endorsed based upon the areas of control selected on the "Data Centre Information" tab.
Note on M8: Liam Newcombe: This column identifies whether this expected practice should be Implemented, Endorsed or both Implemented and Endorsed based upon the areas of control selected on the "Data Centre Information" tab.
Note on N8: Liam Newcombe: This column identifies whether this expected practice should be Implemented, Endorsed or both Implemented and Endorsed based upon the areas of control selected on the "Data Centre Information" tab.
Note on P8: Liam Newcombe: If this is an expected practice that you are not able to implement for this data centre then please describe the reason in this column, e.g. "Customer contracts require lighting to be on for the purposes of recording security cameras"
Note on Q8: Liam Newcombe: If you have entered a dommitted date for the practice please describe your acton plan to achieve compliance in this column
Note on R8: Briefly describe the actions taken to endorse the practice to your suppliers or customers where you have no or partial control over this activity.
Note on T8: Liam Newcombe: If the practice is not yet implemented but you are committing to implement the practice by a specified date then enter that date in this column. You should also check the application date above in C3
Note on U8: Liam Newcombe: If you have implemented the practice to apply to the entire data centre, existing and new IT and M&E then select Implemented in this column. If the specified action requires endorsement then select Endorsed in this column and describe in the "Endorsing Actions Taken" column. If you have split control and are expected to both Implement and Endorse this practice then select I&E. Selecting Implemented or Endorsed in this column is understood to mean that the practice is Implemented or Endorsed for New IT Equipment, New Software and Refit.
Note on B11: John Booth:2022 Establish an approval board containing representatives from all disciplines including Senior Management, IT, M&E Engineering, Applications/Software and Procurement. Require the approval of this group for any significant decision to ensure that the impacts of the decision have been properly understood and an effective solution reached. For example, this could include the definition of standard IT hardware lists through considering the M&E implications of different types of hardware. This group could be seen as the functional equivalent of a change board.
Note on B14: John Booth: 2021 Carry out an audit of existing equipment to maximise any unused existing capability by ensuring that all areas of optimisation, consolidation and aggregation are identified prior to new material investment. The most important element to this in terms of impact is the IT equipment and the severity of impact is related to the frequency of refresh and replacement.
Note on B15: John Booth:2021 Recommend the selection and deployment of mechanical and electrical equipment which does not itself require additional cooling beyond standard office room cooling in normal operation (the exception to this being some UPS batteries). Note: Some UPS batteries require to be kept at lower temperatures to preserve performance and reliability and to maximise operational lifetime
Note on B16: John Booth:2023 Co-location and Managed Service providers should employ charging models and tariffs that encourage the use of best practices and improve energy efficiency. Enterprise operators should that the true cost of data centre services are fully understood and properly reported.
Note on B17: John Booth:2024 Introduce a plan for Life Cycle Assessment (LCA) in accordance with EU guidelines and internationally standardised methodologies. Examples of which would be ISO 14040 and ISO 14044. EN 15978 'Sustainability of construction works - assessment of environmental performance of buildings - calculation method' is also a standard that is considered relevant to this Practice. Note: This Practice aims to reduce overall carbon footprint and improve sustainability rather than directly improve energy efficiency. A list of recommended environmental sustainability practices is available in the CEN/CENELEC document CLC 50600-5-1.
Note on B18: John Booth:2023 Introduce a plan for Environmental Management in accordance with emerging EU guidelines and internationally standardised methodologies. An example of which would be ISO 14001. Consider appointing a cross functional Environmental Sustainability Manager to take responsibility for this initiative.
Note on B19: John Booth:2023 Introduce a plan for Energy Management in accordance with emerging EU guidelines and internationally standardised methodologies. An example of which would be ISO 50001. Note: The Code of Conduct can be used effectively to underpin the expectations and reporting requirements specifically for data centres in relation to ISO 50001. Consider appointing a cross functional Energy Manager to take responsibility for this initiative.
Note on B20: John Booth: Ensure that Asset Management for both IT and mechanical and electrical assets etc. is implemented and controlled according to a standard and accepted methodology. An example of which would be ISO 55000. Understanding the numbers, types and purposes of the assets deployed in a data centre underpins effective energy management.
Note on B21: John Booth (2024): Consider the proportion of energy used by the data centre that comes from renewable / sustainable sources. Recording and reporting on the proportion of sustainable / renewable energy used against the overall energy consumption is expected to become an expected monitoring and reporting requirement in time. Note: Standardised metrics in this area are available as EN 50600-4-3 or ISO/IEC 30134-3. EN 50600-4-3 “Information technology — Data centre facilities and infrastructures — Part 4-3: Renewable Energy Factor” specifies the “Renewable Energy Factor, REF” as the ratio of the renewable energy (in kWh) to the total energy consumption (in kWh). Note: REF covers all renewable energy purchased from the utility (with guarantee of origin) and produced on-site. However, renewable energy produced on-site, that is not consumed on-site and partly or in total sold to the grid, shall be excluded from REF. Note: CLC 50600-5-1 addresses Best Practices for Data Centre Energy Efficiency and Environmental Sustainability. Both are a part of the European EN 50600 Standard series. Note: The EN 50600 series has now been adopted by ISO/IEC as ISO/IEC 22237. Note: ETSI EN 305 200-3-1 KPIREN KPI excludes both energy from grid and energy not consumed on site, in conformance with net zero initiatives.
Note on B22: John Booth: Monitor and report on usage / energy consumption by devices power by IT cabling. IT cabling is increasingly be used to deliver power to devices both inside and outside the data centre. The advantage of this technology is that the same cable can be used for both network connectivity and power. Examples of this include telephony (voice) handsets, cameras, a variety of different environmental sensors even LED lights and lighting control. Note: The risk here is that this power is being taken directly from network switches, which constitute “IT Load”. This needs to be considered when looking at energy usage calculations such as DCiE or PUE which may well give false indications if devices are being powered via IT communications cabling and usage is not being taken in to account. Note: This is particularly true if power is being delivered outside the data centre as might be the case with IP Telephony, network switches in the data centre potentially supplying handsets in nearby office spaces.
Note on B23: John Booth:2023 Consider the type of workload(s) that will be supported both during the design and operation of data centres. Note: Traditionally steady workload levels in data centres have resulted in relatively constant power draws however developments in applications and software is resulting in increasingly fluctuating workloads and even the ability to migrate workloads seamlessly between sites. This not only potentially changes the required equipment resilience and reliability levels at a particular site it also changes the way that the installed power and cooling infrastructure needs to be managed from both a capacity and energy efficiency perspective.
Note on B24: John Booth: Consideration should be given to energy supplies from alternative and sustainable energy sources including fuel cells, wind power, photo-voltaic and shared local-generation using biomass / bio-fuels etc., which might provide a lower carbon footprint, economically attractive and reliable alternative to utility electricity supplies. Note: This Practice aims to reduce overall carbon footprint and improve sustainability rather than provide direct energy efficiency.
Note on B25: John Booth (2021): Ensure that air quality is monitored and managed to ensure that critical equipment is not damaged by particulates or corrosive elements which might impact both IT equipment and cooling equipment in terms of performance, energy efficiency and reliability. This should inform the choice of filters used and the planned replacement schedule as well as the frequency of routine technical cleaning programme (including underfloor and ceiling void areas if applicable). Filter choices should be informed by ISO 16890-1. Note: The ASHRAE white paper ‘2011 Gaseous and Particulate Contamination Guidelines for Data Centers’ recommends that data centre air quality is monitored and cleaned according to ISO 14644-8 Class 8. This can be achieved by routine technical cleaning and simple filtration. Note: Airborne Contaminants including gaseous contaminants should be managed according to ANSI/ISA 71.04-2013.
Note on B26: John Booth: 2021 The data centre technical areas and plant rooms should be considered as an industrial space, designed built and operated with the single primary objective of delivering high availability IT services reliably and efficiently. Note: This objective aims to prevent the energy efficiency of the technical space being compromised by the need for human comfort other than to comply with local statutory requirement and law (Health and Safety etc.). Note: Data Centres are primarily technical spaces, not office space, and should therefore only require the control make up air volumes and environmental conditions to pressurise the spaces in order avoid ingress of particles and contaminants rather than for seated human comfort. This only relates to those areas of the centre intended to hold operational IT equipment or supporting mechanical or electrical infrastructure. These areas should not contain desks or workstations. Note: This is not intended to reduce or impose conditions on dedicated and purpose built office space within the data centre building.
Note on B27: John Booth (2019): Ensure that high quality, accurate O&M manuals, As-Built records, commissioning records, schematics and single lines diagrams are available in order to enable all installed infrastructure and equipment to be maintained as originally designed and operated at optimum levels of efficiency. Accurate documentation and records are essential to the correct operation and use of energy efficiency functions built-In by equipment manufacturers. Updates should be made whenever any settings are changed or equipment is added, replaced or modified. Effective commissioning and delivery of detailed and accurate documentation should be a key part of any project handover. Note: EN 50600-3-1 can be referenced for more detail on this area.
Note on B28: John Booth (2019): Ensure the Data Centre Manager and any appointed Energy Manager has relevant and appropriate training to fulfil an energy efficiency role and have an in-depth appreciation of Best Practices (such as this Code of Conduct). Ensure that both ICT and Facilities personnel are aware of Data Centre energy efficiency Best Practises (such as this Code of Conduct) in order to support organisational strategies to reduce IT energy usage. Remove silos and promote a minimum level of common understanding relating to data centre Operations and Management. An overall training methodology should be defined and delivered to all relevant personnel in order to improve individual personal development and develop suitably qualified and experienced data centre personnel. Note: Properly trained and qualified personnel are essential to efficient data centre operation.
Note on B29: John Booth: 2024 Continue to evaluate the use of energy storage and usage to support Smart Grid. A Smart Grid is a solution that employs a broad range of information technology resources, allowing for a potential reduction in electricity waste and energy costs. This Practice should aim to include ‘Behind the Meter’ Support. Guidance and requirements which are currently being developed by the European Commission may impact this Practice. Smart Grids are referenced by the EED, which should be examined for Practices in this area. EN 50600-5-1 already incorporates a Practice in this area which should be considered for adoption.
Note on B32: Liam Newcombe: Only the level of resilience and therefore availability actually justified by business requirements and impact analysis should be built, or purchased in the case of a collocation customer. 2N infrastructures are frequently unnecessary and inappropriate. If only a single level of resilience is available in the data centre an increased resilience or availability for critical services can be obtained by splitting the IT platform across multiple sites.
Note on B33: Liam Newcombe: It is possible to build a single data centre to provide multiple levels of power and cooling resilience to different floor areas. Many co-location providers already deliver this, for example, optional ‘grey’ power feeds without UPS or generator back up.
Note on B34: Liam Newcombe: The provisioning of excess power and cooling capacity in the data centre drives substantial fixed losses and is unnecessary. Planning a data centre for modular (scalable) expansion and then building out this capacity in a rolling program of deployments is more efficient. This also allows the technology ‘generation’ of the IT equipment and supporting M&E infrastructure to be matched, improving both efficiency and the ability to respond to business requirements.
Note on B35: John Booth (2018) : All areas of the data centre should be designed to maximise the energy efficiency of the facility under partial fill / partial load and variable IT electrical and cooling loads. This is in addition to one off modular provisioning and should consider the response of the infrastructure to dynamic loads. E.G. Appropriately controlled Variable Frequency (or speed) Drive for pumps, fans and compressors.
Note on B36: John Booth (2018) Utilise appropriate levels of resilience within the data centre, IT equipment, software and network levels to achieve the service resilience and availability required by the business demands. Installing high levels of resilience require multiple redundant units which reduce overall energy efficiency.
Note on B40: John Booth:2024 Include the Energy efficiency performance of the IT device as a high priority decision factor in the tender process. This may be through the use of SERT (http://www.spec.org/sert/) or SPECPower. (http://www.spec.org/power_ssj2008/results/) or similar metrics or through application or deployment of specific user metrics more closely aligned to the target environment, which may include service level or reliability components. The power consumption of the device at the expected utilisation or applied workload should be considered in addition to peak performance per Watt figures. Reference ISO/IEC 30134-4 Information technology — Data centres — Key performance indicators — Part 4: IT Equipment Energy Efficiency for servers (ITEEsv). Also ETSI - EN 303 470 Environmental Engineering (EE); Energy Efficiency measurement methodology and metrics for servers
Note on B41: John Booth (2023): Equipment should be purchased that allows for operation within ASHRAE Class A2. If no equipment can be procured which meets the operating temperature and humidity range of Practice 4.1.3 (ASHRAE Class A2), then equipment supporting ASHRAE Class A1 at a minimum may be procured. This range is defined as the To support the restrictive range of operation equipment should be installed in a separate area of the data floor in order to facilitate the segregation of equipment requiring tighter environmental controls as described in Practices 5.1.11, 5.3.4 and 5.3.5. In unusual cases where older technology equipment must be procured due to compatibility and application validation requirements (an example being air traffic control systems), these systems should be considered as subset of this Practice and installed so as not to restrict the operation of other equipment described above. A summary of ASHRAE environmental guidelines can be found at: https://www.ashrae.org/file%20library/technical%20resources/bookstore/supplemental%20files/referencecard_2021thermalguidelines.pdf
Note on B42: John Booth (2023): Include the operating temperature and humidity ranges at the air intake of new equipment as high priority decision factors in the tender process. Equipment should be able to operate and be within warranty for the full ASHRAE Class A2 allowable temperature and humidity range. Vendors are required to publish (not simply make available on request) any restriction to the operating hours within this range for any model or range which restricts warranty to less than continuous operation within the allowable range. To address equipment types which cannot be procured to meet this specification exclusions and mitigation measures are provided in Practices 4.1.2 for new IT equipment, 5.1.11 for existing data centres and 5.3.4 for new build data centres. Directly liquid cooled IT devices are addressed in Practice 4.1.14. A summary of ASHRAE environmental guidelines can be found at: https://www.ashrae.org/file%20library/technical%20resources/bookstore/supplemental%20files/referencecard_2021thermalguidelines.pdf
Note on B43: John Booth (2024): Include the operating temperature and humidity ranges at the air intake of new equipment as high priority decision factors in the tender process. Consider equipment which operates under a wider range of intake temperature and humidity such as that defined in ASHRAE Class A4 (broadly equivalent to ETSI EN 300 019–1-3 Class 3.1). This extended range allows operators to eliminate the capital cost of providing mechanical cooling capability in some hotter climate regions. Note: Many vendors provide equipment whose intake temperature and humidity ranges exceed the minimum sets represented by the described classes in one or more parameters. Operators should request the actual supported range from their vendor(s) and determine whether this presents an opportunity for additional energy or cost savings through extending the operating temperature or humidity range in all or part of their data centre. A summary of ASHRAE environmental guidelines can be found at: https://www.ashrae.org/file%20library/technical%20resources/bookstore/supplemental%20files/referencecard_2021thermalguidelines.pdf
Note on B44: John Booth (2021): Select and deploy IT equipment at the designed power density (per cabinet or m²) of the data centre to avoid running the cooling system outside design parameters. Note: Increasing power density may create cooling and air flow management problems reducing both capacity and efficiency. Power and cooling need to be considered as capacity constraints in addition to physical space as referenced in Practice 5.5.6.
Note on B45: John Booth (2023): When selecting new IT equipment require the vendor to supply at minimum the total system power for a range of temperatures covering the full allowable inlet temperature range for the equipment at 100% load on a specified recognised benchmark such as Linpack, SERT (http://www.spec.org/sert/) or SPECPower http://www.spec.org/power_ssj2008/). Data should be provided for 5°C or smaller steps of inlet temperature. As a minimum comply with the EU Eco Design Directive and Lot 9 amendments to EU Commission regulation for servers and online storage systems. It is also recommended that: Total system power covering the full allowable inlet temperature range under 0% and 50% load on the selected benchmark. These sets of data are shown easily in a single table and single chart will allow a data centre operator to select equipment to meet their chosen operating temperature range without significant increase in power consumption. This Practice is intended to improve the thermal performance of IT equipment by allowing operators to avoid devices with compromised cooling designs and creating a market pressure toward devices which operate equally well at increased intake temperature. Consider referencing and using the current U.S. EPA ENERGY STAR specifications for Servers. Consider referencing and using the current U.S. EPA ENERGY STAR specifications for Data Center Storage.
Note on B46: John Booth (2022): When selecting equipment for installation into racks ensure that the air flow direction matches the air flow design for that area. This is commonly front to rear or front to top. If the equipment uses a different air flow direction to that defined for the area into which it is installed (such as right to left when the rack is intended to be front to back) it should only be used with a correction mechanism such as ducts, or special racks that divert the air flow to the defined direction. Equipment with non standard air flow will compromise the air flow management of the data centre and therefore restrict the ability to increase temperature set points. It is possible to mitigate this issue by segregating such equipment according to Practices 5.1.11, 5.3.4 and 5.3.5
Note on B47: Liam Newcombe: Formally change the deployment process to include the enabling of power management features on IT hardware as it is deployed. This includes BIOS, operating system and driver settings.
Note on B48: John Booth (2021): Provision power and cooling only to the planned power draw of the IT equipment as configured (based on the components actually installed), rather than the Power Supply Unit (PSU) size or nameplate rating. This is intended to avoid over-sizing of electrical infrastructure resulting in a low (partial) load and therefore inefficient operation. Note: This may require changes to the provisioning if the IT equipment performance is increased or upgraded.
Note on B49: John Booth (2022): As a minimum comply with the EU Eco Design Directive and Lot 9 amendments to EU Commission regulation for servers and online storage systems. The Energy Star Labelling programs for IT equipment should be used as a guide to server selection where and when available for that class of equipment. Operators who are able to determine the in-use energy efficiency of hardware through more advanced or effective analysis should select the most efficient equipment for their scenario.
Note on B50: John Booth (2023) : Select equipment with power and inlet temperature reporting capabilities, preferably reporting energy used as a counter in addition to power as a gauge. Where applicable, industry standard reporting approaches should be used such as IPMI, DMTF Redfish and SMASH. To assist in the implementation of temperature and energy monitoring across a broad range of data centres all devices with an IP interface should support one of the following: • SNMP polling of inlet temperature and power draw. Note that event based SNMP traps and SNMP configuration are not required • IPMI polling of inlet temperature and power draw (subject to inlet temperature being included as per IPMI or Redfish) • An interface protocol which the operators’ existing monitoring platform is able to retrieve inlet temperature and power draw data from without the purchase of additional licenses from the equipment vendor The intent of this Practice is to provide energy and environmental monitoring of the data centre through normal equipment churn.
Note on B51: John Booth (2017): Select equipment which provides mechanisms to allow the external control of its energy use. An example of this would be the ability to externally restrict a server’s maximum energy use or trigger the shutdown of components, entire systems or sub-systems.
Note on B52: John Booth (2023): If no alternative is available then select equipment which is free standing or supplied in custom cabinets so that the air flow direction of the enclosures match the airflow design in that area of the data centre. This is commonly front to rear or front to top. Specifically, the equipment should match the hot / cold aisle layout or containment scheme implemented in the facility. Equipment with non-standard air flow can compromise the air flow management of the data centre and restrict the ability to raise temperature set points. It is possible to mitigate this compromise by segregating such equipment according to Practices 5.1.11, 5.3.4 and 5.3.5 Note: Try to avoid free standing equipment as it usually does not allow a well organised airflow through the data centre especially if the major part of the room is equipped with well organised IT equipment mounted in cabinets.
Note on B53: John Booth (2021): Devices whose primary cooling method is not air and are liquid cooled, are not subject to the air environmental requirements specified in 4.1.2 or 4.1.3. Direct liquid cooling is addressed in section 5.6. As described in 5.4.2.9 this Practice applies to devices which deliver cooling liquid directly to the heat removal system of the components such as water cooled heat sinks or heat pipes and not the delivery of cooling liquid to an internal mechanical refrigeration system or in chassis air cooling systems which are required to deliver coolant liquid or air to the IT components within the range specified. Direct liquid cooling may offer advantages in very high density applications such as High Performance Computing (HPC), and may demonstrate some energy efficiency advantages including the useful extraction and potential re-use of ‘waste heat’. Note: ASHRAE offers guidelines for the use of liquid cooling in data centres these are contained in the publication ‘Liquid Cooling Guidelines for Datacom Equipment Centers, Second Edition’.
Note on B54: John Booth (2024): Select IT equipment containing high efficiency AC/DC power converters. These should be rated at 90% power efficiency or better across the range of loads expected for the equipment to be installed. Reference ISO/IEC 30134-4 Information technology — Data centres — Key performance indicators — Part 4: IT Equipment Energy Efficiency for servers (ITEEsv) Also ETSI – EN 303 470 Environmental Engineering (EE); Energy Efficiency measurement methodology and metrics for servers This Practice should also be implemented in line with the IEC 62040-5 standard.
Note on B57: John Booth (2022): Processes should be put in place to require senior business approval for any new service that requires dedicated hardware and will not run on a resource sharing platform. This applies to servers, storage and networking aspects of the service.
Note on B58: John Booth 2021: Determine the business impact of service incidents for each deployed service and deploy only the level of hardware resilience that is fully justified. Ensure that the IT hardware resilience level is agreed by the application owners.
Note on B59: Liam Newcombe: Determine the business impact of service incidents for each IT service and deploy only the level of Business Continuity / Disaster Recovery standby IT equipment and resilience that is actually justified by the business impact.
Note on B60: John Booth (2021): Make the energy use performance of the software a primary selection factor. Whilst forecasting and measurement tools and methods are still being developed, approximations can be used such as the (under load) power draw of the hardware required to meet performance and availability targets. This is an extension of existing capacity planning and benchmarking processes. See “Further development of software efficiency definitions” in section 11.
Note on B61: John Booth (2021): Make the energy use performance of the software a major success factor of the project. Whilst forecasting and measurement tools and methods are still being developed approximations, can be used such as the (under load) power draw of the hardware required to meet performance and availability targets. This is an extension of existing capacity planning and benchmarking processes. Performance optimisation should not be seen as a low impact area to reduce the project budget. See “Further development of software efficiency definitions” in section 11.
Note on B62: John Booth (2021) If software development is being outsourced then include the energy use of the software in the bonus / penalty clauses of the contract. Whilst forecasting and measurement tools and methods are still being developed approximations, could be used such as the (under load) power draw of the hardware required to meet performance and availability targets. This is an extension of existing capacity planning and benchmarking processes. Performance optimisation should not be seen as a low impact area to reduce the project budget. See “Further development of software efficiency definitions” in section 11.
Note on B63: Liam Newcombe: Determine the business impact of short service incidents for each deployed service and replace traditional active / passive server hardware clusters with fast recovery approaches such as restarting virtual machines elsewhere. (this does not refer to grid or High Performance Compute clusters)
Note on B64: John Booth (2024) Set minimum or average targets for the utilisation of IT equipment (servers, networking, storage). Note: This presents substantial uncertainty when considered without the load to power profiles of the equipment, with cloud and mobile services and the increasing ability to relocate the IT compute function dynamically to an alternate location and better serve customers and optimise costs, this becomes more complex and would require substantial work to usefully determine. Note: This is a specialist area which is being examined in detailed by bodies specialising in this field. Reference ISO/IEC 30134-5 Information technology — Data centres — Key performance indicators — Part 5: IT Equipment Utilization for servers (ITEUsv) Also ISO/IEC 21836. Information technology — Data centres — Server energy effectiveness metric (SEEM)
Note on B65: John Booth:2023 When purchasing new cloud services or assessing a cloud strategy, assess the impact on network equipment usage and the potential increase or decrease in energy consumption with the aim of being to inform purchasing decisions. The minimum scope shall include elements inside the data centre. The ambition is to include overall energy consumption and energy efficiency including that related to multiple site operation and the network energy use between those sites.
Note on B68: John Booth (2018): Audit the existing physical and logical estate to establish what equipment is in place and what service(s) it delivers. Consider the implementation of an ITIL type Configuration Management Data base and Service Catalogue. A useful standard and reference to use in support of this Practice could be ISO 55000 See Practice 3.2.7
Note on B69: John Booth: Completely decommission and remove any equipment that is not required or used to support services no longer in use. Installed hardware should be regularly examined to ensure that it is still required and supporting active services.
Note on B70: Liam Newcombe: Servers which cannot be decommissioned for compliance or other reasons but which are not used on a regular basis should be virtualised and then the disk images archived to a low power media. These services can then be brought online when actually required
Note on B71: John Booth (2022) : Existing services that do not achieve high utilisation of their hardware should be consolidated through the use of resource sharing technologies to improve the use of physical resources. This applies to servers, storage and networking devices.
Note on B72: John Booth 2021 Identify services whose business value or criticality is low and that do not justify the financial or environmental overhead. Consider decommissioning or archiving these services or remove to locations with less reliability / resilience to reduce energy and financial overhead.
Note on B73: John Booth (2022): Servers, networking and storage equipment that is idle for significant time and cannot be virtualised or archived should be shut down or put into a low power ‘sleep’ state. Complete removal should also be considered. It will be necessary to validate the ability of legacy applications and hardware to survive these state changes without loss of function or reliability.
Note on B74: John Booth:2023 Consider resource management systems capable of analysing and optimising where, when and how IT workloads are executed and their consequent energy use. This may include technologies that allow remote deployment or delayed execution of jobs or the movement of jobs within the infrastructure to enable shutdown of components, entire systems or sub-systems. The desired outcome is to provide the ability to limit localised heat output or constrain system power draw to a fixed limit, at a data centre, row or cabinet level.
Note on B75: John Booth (2022): Identify the allowable intake temperature and humidity ranges for existing installed IT equipment. Equipment with restrictive intake temperature ranges should be identified so that it may be either marked for replacement with newer equipment capable of a wider intake range or moved and dealt with according to Practices “Equipment segregation” (5.1.11) and “Separate environmental zones” (5.3.4 and 5.3.5)
Note on B78: Liam Newcombe: Develop a data management policy to define which data should be kept, for how long and at what level of protection. Communicate the policy to users and enforce. Particular care should be taken to understand the impact of any data retention requirements,
Note on B79: Liam Newcombe: Provide users with multiple data storage areas which are clearly identified by their retention policy and level of data protection. Communicate this policy to users to enable them to store data in an area which matches the required levels of protection and retention. This is particularly valuable where strong retention requirements exist as it allows data subject to those requirements to be separated at source presenting substantial opportunities for cost and energy savings. Where possible automate the application of these policies.
Note on B80: Liam Newcombe: Create a tiered storage environment utilising multiple media types delivering the required combinations of performance, capacity and resilience. Implement clear guidelines on usage of storage tiers with defined SLAs for performance and availability. Consider a tiered charging model based on usage at each tier.
Note on B81: John Booth 2024: When selecting storage hardware evaluate the energy efficiency in terms of the service delivered per Watt between options. This may be deployment specific and should include the achieved performance and storage volume per Watt as well as additional factors where appropriate, such as the achieved levels of data protection, performance availability and recovery capability required to meet the business service level requirements defined in the data management policy. Evaluate both the in-use power draw and the peak power of the storage device(s) as configured, both impact per device cost and energy consumption through provisioning. As a minimum comply with the EU Eco Design Directive and Lot 9 amendments to EU Commission regulation for servers and online storage systems.
Note on B82: Liam Newcombe: Implement an effective data identification and management policy and process to reduce the total volume of data stored. Consider implementing ‘clean up days’ where users delete unnecessary data from storage.
Note on B83: Liam Newcombe: Implement the data management policy to reduce the number of copies of data, both logical and physical (mirrors). Implement storage subsystem space saving features, such as space efficient snapshots / copies or compression. Implement storage subsystem thin provisioning features where possible.
Note on B87: John Booth (2017): As the power densities and air flow volumes of IT equipment have increased it has become necessary to ensure that equipment shares an air flow direction, within the cabinet, in adjacent cabinets and across aisles. The hot / cold aisle concept aligns equipment air flow to create aisles between cabinets that are fed cold air from which all of the equipment draws intake air in conjunction with hot aisles with no cold air feed to which all equipment exhausts air. Reinforce Hot / Cold aisle design with empty but fully blanked cabinets (or solid doors) rather than leaving gaps in aisles. Note: This best practice applies to New IT Equipment & New Build & Retrofit
Note on B88: John Booth (2021) : There are a number of design concepts whose basic intent is to contain and separate the cold air from the heated return air on the data floor; • Hot aisle containment • Cold aisle containment • Contained cabinet supply, • Contained room return and room supply. • Contained cabinet return, and cabinet chimneys. • Contained cabinet supply, Contained cabinet return Note: Failure to contain air flow results in both a reduction in achievable cooling efficiency and an increase in risk. Changes in IT hardware and IT management tools mean that the air flow and heat output of IT devices is no longer constant and may vary rapidly due to power management and workload allocation tools. This may result in rapid changes to data floor air flow pattern and IT equipment intake temperature which cannot be easily predicted or prevented. This Practice supersedes Practice 5.1.1 when implemented.
Note on B89: John Booth (2021): Where hot / cold aisle separation is already in use but there is no containment of hot or cold air it is possible to retrofit to provide basic separation for example using curtains or other methods. Care should be taken to assess and verify fire system requirements and regulations.
Note on B90: Liam Newcombe: Installation of blanking plates where there is no equipment to reduce cold air passing through gaps in the rack. This also reduces air heated by one device being ingested by another device, increasing intake temperature and reducing efficiency.
Note on B91: John Booth: Installation of aperture brushes (draught excluders) or cover plates to cover all air leakage opportunities in each rack. This includes; • floor openings at the base of the rack • Gaps at the sides, top and bottom of the rack between equipment or mounting rails and the perimeter of the rack
Note on B92: John Booth (2024) Solid doors should be replaced (where cooling ventilation is necessary), with perforated doors to ensure adequate cooling airflow. Solid doors impede the cooling airflow and promote recirculation within the enclosed cabinet increasing equipment inlet temperatures. ISO/IEC 14763-2 recommends a minimum of at least 66% perforated area.80% is considered an ideal target by other authorities.
Note on B93: John Booth (2021) Close all unwanted apertures in the raised floor. Review placement and opening factors of vented tiles to reduce bypass. Maintain unbroken rows of cabinets to prevent re-circulated air. If necessary fill with empty fully blanked racks. Managing unbroken rows is especially important in hot and cold aisle environments. Any opening between the aisles will degrade the separation of hot and cold air.
Note on B94: John Booth (2021): Review the placement and level of obstruction created by cabling, cable trays and other structures in the air flow paths, these obstruct airflow and create turbulence, increasing the resistance and increasing the energy requirements of air movement and may increase velocities, causing negative pressure. Ensure that the under floor area is as free of obstructions as possible. The use of overhead cabling trays can substantially reduce the level of obstruction.
Note on B95: Liam Newcombe: Consider the use of return plenums to return heated air from the IT equipment to the air conditioning units
Note on B96: John Booth (2021): It is common to use the voids in the raised floor, suspended ceiling or both in a data centre to feed cold air to equipment or extract hot air from the equipment. Where they are used, increasing the size of these spaces can significantly reduce fan losses moving the air.
Note on B97: John Booth (2022): Deploy groups of equipment with substantially different environmental requirements and / or equipment airflow direction in a separate area. Where equipment has different environmental requirements it is preferable to provide separate environmental controls. This objective of this practice is to address the issue of the data centre cooling plant settings being constrained by the equipment with the most restrictive environmental range or poor air flow control as this compromises the efficiency of the entire data centre. This practice applies to IT, mechanical and electrical equipment installed in the data centre. Note: This best practice applies for New IT Equipment and New Build & Retrofit.
Note on B98: John Booth (2022): Investigate operating cooling unit fans to ensure a slight oversupply of air compared to IT equipment flow demand to minimise recirculation whilst avoiding oversupply of air volume (results in bypass and fan energy wastage). This principle is particularly applicable contained systems. In contained air systems, ensure that there is a slightly positive pressure (preferably no more than 5Pa) in the cold air stream with respect to the hot air stream.
Note on B101: John Booth (2021): Cooling plant should be installed in a modular arrangement allowing operators to shut down unnecessary equipment. This should then be part of the review at each cooling load change. Design to maximise the part load efficiency as described in sections 3.3.4, 5.4.2.3 and 5.4.2.4
Note on B102: John Booth: If the facility is not yet fully populated or space has been cleared through consolidation non variable plant such as fixed speed fan CRAC / CRAH units can be turned off in the empty areas. Note that this should not be applied in cases where operating more plant at lower load is more efficient, e.g. variable speed drive CRAC / CRAH units.
Note on B103: Liam Newcombe: The availability of cooling including the placement and flow of vented tiles should be reviewed before each IT equipment change to optimise the use of cooling resources.
Note on B104: Liam Newcombe: Periodically review the IT equipment and cooling deployment against strategy.
Note on B105: John Booth (2017): Ensure that CRAC units in occupied areas have appropriate and consistent temperature and relative humidity settings to avoid units working against each other. For example many CRAC units now have the option to connect their controls and run together when installed in the same area. Care should be taken to understand and avoid any potential new failure modes or single points of failure that may be introduced.
Note on B106: John Booth (2021): Consider implementing control systems that take multiple factors including cooling load, data floor air temperature and external air temperature into account to optimise the cooling system, (e.g. chilled water loop temperature) in real time. Control should be according to an agreed strategy.
Note on B107: John Booth (2023): Implement effective regular maintenance of the cooling system in order to conserve or achieve a “like new condition” is essential to maintain the designed cooling efficiency of the data centre. Examples include the following: belt tension, condenser coil fouling (water or air side), evaporator fouling etc. This includes regular filter changes to maintain air quality and reduce friction losses along with the routine monitoring of air quality and a regular technical cleaning regime (including under-floor areas if applicable).
Note on B108: John Booth (2022): Review and if possible increase the chilled water temperature set points to maximise the use of free cooling and reduce compressor energy consumption. Seasonal impact should be taken into account where applicable. Set points should be raised together with supply air flow set points to avoid reducing capacity. Review and if useful increase the chilled water temperature difference to reduce the water flow and thereby to reduce pump energy consumption. Where a DX system is used the evaporator temperatures should be reviewed. Electronic Expansion Valves (EEVs) allow better control and permit higher evaporator temperatures than Thermostatic Expansion Valves (TEVs).
Note on B111: John Booth (2023): Data Centres should be designed and operated at their highest efficiency to deliver intake air to the IT equipment within the ASHRAE Class A2 allowable range for Data Centres. Operations in this range enable energy savings by reducing or eliminating overcooling. Note: Some data centres may contain equipment with legacy environmental ranges as defined in 4.1.2, the maximum temperature for these facilities will be restricted by this equipment until segregation can be achieved as described in Practices 5.1.11, 5.3.4 and 5.3.5. Note: Additional Best Practices for airflow management as defined in section 5.1 may need to be implemented at the same time to ensure successful operations. Note: Some, particularly older, IT equipment may exhibit significant increases in fan power consumption as intake temperature is increased. Validate that your IT equipment will not consume more energy than is saved in the cooling system. A summary of ASHRAE environmental guidelines can be found at: https://www.ashrae.org/file%20library/technical%20resources/bookstore/supplemental%20files/referencecard_2021thermalguidelines.pdf
Note on B112: John Booth (2023): Reduce the lower humidity set point(s) of the data centre within the ASHRAE Class A2 range to reduce the demand for humidification. Review and if practical increase the upper humidity set point(s) of the data floor within the current A2 humidity range of decrease the dehumidification loads within the facility. The relevant standard is the ASHRAE Class A2 allowable range for Data Centers. Note: Some data centres may contain equipment with legacy environmental ranges as defined in 4.1.2, the humidity range for these facilities will be restricted by this equipment until segregation can be achieved as described in Practices 5.1.11, 5.3.4 and 5.3.5. Controlling humidity within a wider range of humidity ratio or relative humidity can reduce humidification and dehumidification loads and therefore energy consumption. A summary of ASHRAE environmental guidelines can be found at: https://www.ashrae.org/file%20library/technical%20resources/bookstore/supplemental%20files/referencecard_2021thermalguidelines.pdf
Note on B113: John Booth 2024: Where appropriate and effective, Data Centres can be designed and operated within the air inlet temperature and relative humidity ranges of 5°C to 40°C and 5% to 80% rh, non-condensing respectively, and under exceptional conditions up to +45°C as described in ETSI EN 300 019–1-3 Class 3.1. Note: Using the full range up to 40°C or 45°C will allow for the complete elimination of refrigeration in most climates allowing the operator to eliminate the capital and maintenance cost of the cooling systems.
Note on B114: John Booth (2022): Where a data centre houses both IT equipment compliant with the extended range of Practice 4.1.3 and other equipment which requires more restrictive temperature or humidity control as described in Practice 4.1.2, separate areas should be provided. These areas should have separate environmental controls and may use separate cooling systems to facilitate optimisation of the cooling efficiency of each zone. Examples are equipment which; • Requires tighter environmental controls to maintain battery capacity and lifetime such as UPS • Requires tighter environmental controls to meet archival criteria such as tape • Requires tighter environmental controls to meet long warranty durations (10+ year) The objective of this Practice is to avoid the need to set the data centre cooling plant for the equipment with the most restrictive environmental range and therefore compromising the efficiency of the entire data centre
Note on B115: John Booth (2022): Customers requiring extremely tight environmental control or items such as legacy equipment should not compromise the entire data centre for specific items of equipment. Service providers should design in such a way that discrete areas may be offered to customers with additional “close control” cooling equipment in order to match specific requirements this and therefore offer a tighter SLA that would inevitably involve reduced energy efficiency. These legacy equipment support areas may be differentially priced to include the capital and operational (Metered), cost overhead of supporting a less energy efficient legacy environment as an incentive for customers to install IT equipment in more efficient areas and consider the options for more energy efficient delivery of IT services.
Note on B118: John Booth (2021): External air is used to cool the facility with different operating modes usually deployed. When outdoor conditions are cold exhaust air can be re-circulated and mixed with intake air to control supply air temperature and humidity. In many cases full mechanical cooling / refrigeration capacity is required as a backup to allow operation during periods of high airborne pollutant (E.G. External fires). For this reason special attention should be focussed on external air quality monitoring and filtration. Additional backup mechanical cooling with chiller or CRAC may also be considered to ensure cooling at extreme ambient temperature and humidity conditions or for system redundancy. Note: This design tends to have the lowest temperature difference between external temperature and IT supply air. Note: IT equipment is likely to be exposed to a large humidity range to allow direct air free cooling to work effectively. The achievable free cooling hours are directly constrained by the chosen upper humidity limit.
Note on B119: John Booth (2018) : Re circulated air within the facility is primarily passed through an air to air heat exchanger against external air (may have adiabatic cooling) to remove heat to the atmosphere. A variation of this is a thermal wheel, quasi –indirect free cooling system. This design tends to have a low temperature difference between external temperature and IT supply air. Note that the operating IT equipment humidity range may be well controlled at negligible energy cost in this type of design. Note that air filtration demand is lower compared to direct air free cooling as data centre air is circulating and no external air is induced.
Note on B120: John Booth (2018): Chilled water cooled by the external ambient air via a free cooling coil. This may be achieved by dry coolers or by evaporative assistance through spray onto the dry coolers. This design tends to have a higher temperature difference between external temperature and IT supply air. Note that the operating IT equipment humidity range may be well controlled at negligible energy cost in this type of design. Note that in this system additional backup mechanical cooling with chiller or CRAC may be considered to ensure cooling at extreme ambient temperature and humidity conditions or for system redundancy.
Note on B121: John Booth (2018): Chilled water is cooled by the external ambient conditions via cooling towers or dry coolers, the dry coolers may have evaporative assistance. This chilled water is supplied to the free cooling coil of the CRAC if its temperature is low enough to provide full free cooling or at least partial free cooling. In addition it is supplied to the plate condenser of the CRAC´s closed DX circuit when compressor operation is needed to provide sufficient cooling. This design tends to have a higher temperature difference between externa temperature and IT supply air restricting the economiser hours available and increasing energy overhead. Note that partial free cooling (Mix mode) starts a few degrees below the return air temperature of the CRAC. Note that the operating IT equipment humidity range may be well controlled at negligible energy cost in this type of design.
Note on B122: John Booth (2018): Chilled water is produced by the free cooling chiller either through the free cooling coils in the chiller if ambient temperatures are low or with compressors in operation at higher ambient temperatures. This chilled water is supplied to the CRAH in the data centre. This design tends to have a higher temperature difference between external temperature and IT supply air restricting the economiser hours available and increasing energy overhead. Note that partial free cooling (Mix mode) starts a few degrees below the return water temperature. Note that the operating IT equipment humidity range may be well controlled at negligible energy cost in this type of design.
Note on B123: John Booth: Cooling unit chilled water is cooled via a plate heat exchanger to the condenser water circuit passing through dry/adiabatic coolers / cooling towers. This design usually has a highest difference between the external temperature and IT supply air due to the additional heat exchange process.
Note on B124: John Booth (2022) Evaluate alternative forms of cooling where available, practical to utilise and offer genuine energy efficiency including Ground Source Cooling from rivers, lakes, boreholes and seawater etc.
Note on B125: John Booth (2018): Investigate the installation of free cooling in all new builds and retrofits or upgrades of cooling systems.
Note on B129: John Booth (2021): Where refrigeration (1) is installed make the Coefficient Of Performance (COP) or Energy Efficiency Ratio (EER) of chiller systems through their likely working range a high priority decision factor during procurement of new plant. (1) Note that this refers to mechanical compressors and heat pumps, any device which uses energy to raise the temperature of the rejected heat
Note on B130: John Booth: Evaluate the opportunity to decrease condensing temperature and increase evaporating temperature; reducing delta T between these temperatures means less work is required in cooling cycle hence improved efficiency. These temperatures are dependent on required IT equipment intake air temperatures and the quality of air flow management (see Temperature and Humidity Settings).
Note on B131: John Booth (2018): Optimise the facility for the partial load it will experience for the majority of operational time rather than max load. Examples are exploiting the heat exchange area, reducing fan energy consumption, sequencing chillers and operating cooling towers with shared load.
Note on B132: John Booth: Using variable speed control reduces energy consumption for these components in the part load condition where they operate for much of the time. Consider new or retrofit of Electrically Commutated (EC) motors which are significantly more energy efficient than traditional AC motors across a wide range of speeds. In addition to installing variable speed drives it is critical to include the ability to properly control the speed according to demand. It is of limited value to install drives which are manually set at a constant speed or have limited control settings.
Note on B133: John Booth (2018): Cooling designs should be chosen which allow the use of as much “Free Cooling” as is possible according to the physical site constraints, local climatic or regulatory conditions that may be applicable. Select systems which facilitate the use of free cooling. In some data centres it may be possible to use direct or indirect air side free cooling. Others may not have sufficient available space and may require a chilled liquid cooling system to allow the effective use of economised cooling.
Note on B134: John Booth: In buildings which are principally designed to provide an appropriate environment for IT equipment, and that have cooling systems designed to remove heat from technical spaces, do not share chilled water systems with human comfort cooling in other parts of the building. The required temperature to achieve latent cooling for comfort cooling is substantially below that required for sensible cooling of the data centre and will compromise the efficiency of the data centre cooling system. If comfort cooling remains a requirement consider the use of heat pumps to provide either cooling or heating for office area comfort.
Note on B135: John Booth:2024 Where other equipment requires a more restrictive temperature or humidity control range than the IT equipment this should not be permitted to dictate the set points of the cooling system responsible for the IT equipment.
Note on B136: John Booth: Chilled water systems configured with dual pumps, one active, one on standby, can be reviewed for improved energy efficiency during operation. Using the pump manufacturers’ graphs of energy use vs pump speed, evaluate running two pumps in parallel vs a single pump running at a higher speed. If beneficial implement the running of two low speed pumps to reduce energy usage while achieving the same target flow rate and pressure.
Note on B140: John Booth: Many old CRAC / CRAH units operate fixed speed fans which consume substantial power and obstruct attempts to manage the data floor temperature. Variable speed fans are particularly effective where there is a high level of redundancy in the cooling system, low utilisation of the facility or highly variable IT electrical load. These fans may be controlled by factors such as the supply or return air temperature or the chilled air plenum pressure. Note that CRAC / CRAH units with fixed speed compressors have minimum flow requirements which constrain the minimum operating load and therefore minimum air flow.
Note on B141: John Booth: Controlling on supply temperature ensures an even supply air temperature independent of the load on each CRAC / CRAH unit. Historically many CRAC / CRAH units were controlled on return temperature which is no longer considered best practice.
Note on B142: Liam Newcombe: It is possible to achieve efficiency gains by running CRAC units with variable speed fans in parallel to reduce the total electrical power necessary to achieve the required air movement as electrical power is not linear with air flow. Care should be taken to understand any new failure modes or single points of failure that may be introduced by any additional control system.
Note on B143: Liam Newcombe: In the absence of variable speed fans it is possible to turn entire CRAC units on and off to manage the overall air flow volumes. This can be effective where there is a high level of redundancy in the cooling system, low utilisation of the facility or highly variable IT electrical load.
Note on B144: John Booth: The only humidity control that should be present in the data centre is that on fresh “Make Up” air coming into the building and not on re-circulating air within the equipment rooms. Humidity control at the CRAC/CRAH unit is unnecessary and undesirable. Humidity control should be centralised. Do not install humidity control at the CRAC/CRAH unit on re-circulating air. Instead control the specific humidity of the make-up air at the supply AHU. The chilled water loop or DX evaporator temperature should in any case be too high to provide de-humidification. When purchasing new CRAC/CRAH units select models which are not equipped with humidity control capability, including any reheat capability, this will reduce both capital and on-going maintenance costs.
Note on B145: John Booth (2018): Air volumes required by IT equipment not only depend on the IT load (kW) but also on the IT equipment delta-T, which will also vary with utilisation. Consider these factors, plus likely future utilisation and bypass to size the cooling units design flow rates. As air flow is inversely proportional to delta T for the same load, if the IT delta-T is overestimated, this will result in undersized CRAC / CRAH air volumes and potential air management problems. Additionally if it is underestimated, CRAC / CRAH air volumes will be oversized which makes low part load inefficient operation and air bypass more likely.
Note on B148: John Booth (2021): Originally 5.4.2.9 In place of air cooling it is possible to directly liquid cool part or all of some IT devices. This can provide a more efficient thermal circuit and allow the coolant liquid system temperature to be substantially higher, further driving efficiency, allowing for increased or exclusive use of free cooling or heat re use. Note: This Practice applies to devices which deliver cooling liquid directly to the heat removal system of the components such as water cooled heat sinks or heat pipes and not the delivery of cooling liquid to an internal mechanical refrigeration plant or in-chassis air cooling systems. Note: ASHRAE offers guidelines for the use of liquid cooling in data centres. These can be found in the publication ‘Liquid Cooling Guidelines for Datacom Equipment Centers, Second Edition’
Note on B151: John Booth (2022) : Evaluate the possibility of providing low grade heating to industrial space or to other targets such as adjacent office space fresh air directly from heat rejected from the data centre. This does not reduce the energy consumed by the data centre itself but does offset the total energy overhead by potentially reducing energy use elsewhere.
Note on B152: John Booth (2021) Where it is not possible to directly re use the waste heat from the data centre due to the temperature being too low it can still be economic to use additional heat pumps to raise the temperature to a useful point. This can potentially supply office, district and other heating needs.
Note on B153: John Booth 2021: Reduce or eliminate the electrical preheat loads for generators and fuel storage by using warm exhaust air from the data floor to maintain temperature in the areas housing generators and fuel storage tanks and office areas.
Note on B154: John Booth (2024): The opportunity for the reuse of waste heat from data centres is referenced by ISO/IEC 30134-6 Information technology — Data centres — Key performance indicators — Part 6: Energy Reuse Factor (ERF)
Note on B155: John Booth 2021: Consider installing ‘Capture Ready’ Infrastructure to take advantage of, and distribute, available waste heat during new build and retrofit projects.
Note on B159: Liam Newcombe: It is now possible to purchase modular (scalable) UPS systems across a broad range of power delivery capacities. Physical installation, transformers and cabling are prepared to meet the design electrical load of the facility but the sources of inefficiency (such switching units and batteries) are installed, as required, in modular units. This substantially reduces both the capital cost and the fixed overhead losses of these systems. In low power environments these may be frames with plug in modules whilst in larger environments these are more likely to be entire UPS units.
Note on B160: John Booth (2022): If static AC UPS systems are to be installed select energy efficient UPS systems that are compliant with the “elite requirements” of the 2021 version of the EU Code of Conduct on Energy Efficiency of AC Uninterruptible Power Systems. A UPS compliant to this Code of Conduct requirement should also be compliant to IEC 62040 series for UPS systems, which also provides environmental operating conditions. A UPS conforming to this standard should be able to perform as rated when operating within the following minimum ambient ranges: Temperature 0°C to +40°C. Relative Humidity 20% to 80% Note: Rotary and Direct Current UPS systems are not included in the 2021 version of the EU Code of Conduct on AC Uninterruptible Power Systems, but this does not in any way suggest that rotary or Direct Current UPS should not be used, rather that these technologies are not currently covered by an EU Code of Conduct providing shared evidence of meeting high efficiency requirements for these systems.
Note on B161: John Booth (2018): Deploy UPS units in their most efficient operating modes where appropriate. Note Use of alternative UPS technologies such as rotary or direct current systems may be considered. The comparison and evaluation of the technologies shall be based on latest and non-biased information about available products in the market. Some UPS systems may have technologies allowing energy optimisation at partial load levels and these shall be taken into account as appropriate for the application. This may also be particularly relevant for any UPS system feeding mechanical loads e.g. CRAC/CRAH fans.
Note on B162: John Booth (2022): Isolation transformers in power distribution to IT equipment down to 120V are typically not required in Europe and should be eliminated from designs as they introduce additional transformer losses unnecessarily.
Note on B163: John Booth 2022: Electrical infrastructure should remain energy efficient under partial fill and variable IT electrical loads as described in Practice 3.3.4.
Note on B167: John Booth: When using engine heaters to keep generators ready for rapid starts, consider reducing the engine heater set-point. Block heaters for the Standby Generators should be controlled to only operate when the temperature conditions warrant it. Consult manufacturer to understand risk / reliability implications.
Note on B168: John Booth 2021: Monitor, understand and manage the consequences of the Power Factors of both the Mechanical and Electrical infrastructure and installed IT equipment within the data centre. Poor Power Factor management can lead to higher cable losses and also introduce significant risk to the continuity of power supply. Low cost power supplies often have very poor Power Factors with little or no correction. These can build up to introduce electrical inefficiency and risk. Poor power factor can result in penalties and extra charges imposed by the grid provider. Note: Consider the use of Power Factor Correction where appropriate.
Note on B172: John Booth 2021 Lights should be turned off, preferably automatically whenever areas of the building are unoccupied, for example switches which turn off lighting a specified time after manual activation. Motion detector activated lighting is generally sufficient to support security camera systems.
Note on B173: John Booth (2024) Low energy lighting systems should be used in the data centre. LED lighting is a good example and a simple retrofit.
Note on B174: John Booth: Use pale / light colours on walls, floors fixtures and fittings including cabinets etc. to reduce the amount of lighting required to illuminate a data hall and therefore the energy consumed for lighting. This will also ensure good levels of visibility both throughout the hall and within cabinets.
Note on B175: John Booth:2024 Select Mechanical and Electrical equipment with direct local metering of power usage and/or temperature reporting capabilities (where appropriate), preferably reporting energy used as a counter in addition to power as a gauge. To assist in the implementation of temperature and energy monitoring across a broad range of data centre infrastructure all monitoring devices installed should be able to use existing networks and operate on an Open Protocol basis. This interface protocol should enable all operators’ existing monitoring platform to be able to retrieve data from the installed meters without the purchase of additional licenses from the equipment vendor. The intent of this Practice is to provide energy and environmental monitoring of the data centre throughout the entire infrastructure with increasing levels of granularity.
Note on B179: Liam Newcombe: Heat generating Mechanical and Electrical plant should be located outside the cooled areas of the data centre wherever possible to reduce the loading on the data centre cooling plant.
Note on B180: John Booth: Where air movement is used to cool the IT equipment, insufficient ceiling height will frequently obstruct the use of efficient air cooling technologies such as raised floor, suspended ceiling, aisle containment or ducts in the data centre.
Note on B181: John Booth: The physical layout of the building should not obstruct or restrict the use of free cooling (either air or water), or other equipment with an economisation / free cooling mode.
Note on B182: Liam Newcombe: Cooling equipment, particularly dry (/adiabatic) coolers should be located in an area of free air movement to avoid trapping it in a local hot spot. Ideally this equipment should also be located in a position on the site where the waste heat does not affect other buildings and create further demand for air conditioning.
Note on B183: John Booth: Minimise solar heating (insolation), of the cooled areas of the data centre by providing shade or increasing the albedo (reflectivity) of the building through the use of light coloured roof and wall surfaces. Shade may be constructed, provided by utilising natural features including “green roof” systems. Effective insulation can be provided by using suitable wall and roof coverings. Additionally do not have external windows in the data centre. Failure to protect against solar heating (insolation) will result in additional cooling requirements.
Note on B184: Liam Newcombe: Minimise solar heating of the cooled areas of the data centre by providing shade or increasing the albedo (reflectivity) of the building through the use of light coloured roof and wall surfaces. Shade may be constructed, provided by trees or “green roof” systems.
Note on B187: John Booth: 2024 Locating the data centre where there are available uses for waste heat can save substantial energy. Heat recovery can be used to heat residential or office space, industrial spaces, hydroponic farming, swimming pools, fish farms, grain and biomass drying etc.
Note on B188: John Booth (2022): Free and economised cooling technologies are more effective in areas of low ambient external temperature and or humidity. Note that most temperature climates present significant opportunity for economised cooling and zero refrigeration.
Note on B189: John Booth (2018) : Free cooling is particularly impacted by high external humidity as dehumidification becomes necessary. Many economiser technologies (such as evaporative cooling) are also less effective.
Note on B190: John Booth (2021): Locating the data centre near a source of free ground source cooling such as a river or lake etc. subject to local environmental regulation
Note on B191: John Booth: Locating the data centre close to the power generating plant can reduce transmission losses.
Note on B194: John Booth: Capture and storage of rain water for evaporative cooling or other non-potable purposes may reduce overall energy consumption
Note on B195: John Booth 2021: Use of other local non-utility or ‘Grey’ water sources for evaporative cooling or other non-potable purposes may reduce overall energy consumption
Note on B196: John Booth 2024: The site should meter water consumption from all sources. The site should seek to use this data to manage and reduce overall water consumption, particularly in areas where fresh water is a scarce resource. Note: Water consumption cannot be directly compared with energy efficiency unless the energy intensity of the water source is understood. Comparing water consumption between buildings is therefore not useful. Note: Reporting should be based on ISO/IEC 30134-9 (WUE)
Note on B200: John Booth (2022): Install metering equipment capable of measuring the total energy use of the data centre, including all power conditioning, distribution and cooling systems. Again, this should be separate from any non data centre building loads. Note that this is required for CoC reporting
Note on B201: John Booth (2022): Install metering equipment capable of measuring the total energy delivered to IT systems, including power distribution units. This may also include other power feeds where non UPS protected power is delivered to the racks. Note that this is required for CoC reporting.
Note on B202: Liam Newcombe: Install metering equipment at room level capable of indicating the supply air temperature and humidity for the IT equipment.
Note on B203: Liam Newcombe: Collect data from CRAC units on supply or return (dependent upon operating mode) air temperature and humidity.
Note on B204: Liam Newcombe: Improve visibility and granularity of data centre infrastructure overheads
Note on B205: Liam Newcombe: Improve visibility of IT energy consumption by metering at the rack level and individual power strips.
Note on B206: John Booth: Improve visibility of air supply temperature in existing hot / cold aisle environments to assist in recognising and dealing with air flow management issues and both over-cooling and under-cooling of IT equipment. Note that this would be applicable in both contained and non-contained aisles.
Note on B207: John Booth: Improve granularity and reduce metering cost by using built in device level metering of intake and / or exhaust air temperature as well as key internal component temperatures. Note that most new servers provide this feature as part of the basic chipset functionality.
Note on B208: John Booth: Improve granularity and reduce metering cost by using built in IT device level metering of energy consumption. Note that most new servers provide this feature as part of the basic chipset functionality.
Note on B211: John Booth: Entry level energy, temperature and humidity (dry bulb temperature, relative humidity and dew point temperature) reporting can be performed with periodic manual readings of measurement and metering equipment. This should occur at regular times, ideally at peak load. Note that energy reporting is already mandated for Code of Conduct reporting requirements also that automated readings are considered to be a replacement for this Practice when applying for Participant status.
Note on B212: Liam Newcombe: Automated daily readings enable more effective management of energy use. Supersedes Periodic manual readings.
Note on B213: Liam Newcombe: Automated hourly readings enable effective assessment of how IT energy use varies with IT workload Supersedes Periodic manual readings and Automated daily readings.
Note on B214: John Booth: Require collection and logging of full economiser, partial economiser and full refrigerant and compressor based cooling hours throughout the year. The intent being to record the amount or time and energy spent running on mechanical refrigerant and compressor based cooling versus the use of free cooling in order to reduce the amount of time spent on mechanical cooling during the year. The site design, cooling system operational setpoints and IT equipment environmental control ranges should allow the data centre to operate without refrigeration for a significant part of the year with no refrigeration for the IT cooling load as evaluated against a Typical Meteorological Year for the site. Note that this refers to mechanical compressors and heat pumps, any device which uses energy to raise the temperature of the rejected heat.
Note on B217: John Booth (2024) : Minimum reporting consists of periodic written reports on energy consumption and environmental ranges. All written reports and submissions should reference the Category being reported and ensure that the required method of data collection and calculation determined by the Standardised ISO KPIs from the ISO/IEC 30134 series (or EN 50600-4-X equivalent), should be used in all reports, written or otherwise if reported. The Standardised KPIs include PUE, pPUE, REF, ITEESV, ITEUSV, ERF, CER, CUE, WUE. Note: Determining the averaged DCiE or PUE over the reporting period is already mandated by the Code of Conduct reporting requirements. This report may be produced by an automated system. Note: All DCiE and PUE calculations should be completed according to the guidelines set out by EN 50600-4-2 which is equivalent to ISO/IEC 30134-2. EN 50600-4-2 “Information technology — Data centre facilities and infrastructures — Part 4-2: Power Usage Effectiveness”. Note: Different categories of PUE ranging from 0 to 3 representing increasing levels of reporting granularity.
Note on B218: John Booth (2017): An automated energy and environmental reporting console to allow M&E staff to monitor the energy use and efficiency of the facility provides enhanced capability. Averaged and instantaneous DCIE or PUE are reported. This supersedes Written Report. See Note in section 9.3.1 above with regard to method of calculation.
Note on B219: John Booth: An integrated energy and environmental reporting capability in the main IT reporting console allows integrated management of energy use and comparison of IT workload with energy use. Averaged, instantaneous and working range DCIE or PUE are reported and related to IT workload. Supersedes Written Report and Energy and environmental reporting console. This reporting may be enhanced by the integration of effective physical and logical asset and configuration data. See Note in section 9.3.1 above with regard to method of calculation.
Note on B220: John Booth: Require reporting of full economiser, partial economiser and full refrigerant and compressor based cooling hours throughout the year. The intent being to report the amount or time and energy spent running on mechanical refrigerant and compressor based cooling versus the use of free cooling in order to reduce the amount of time spent on mechanical cooling during the year. The site design, cooling system operational setpoints and IT equipment environmental control ranges should allow the data centre to operate without refrigeration for a significant part of the year with no refrigeration for the IT cooling load as evaluated against a Typical Meteorological Year for the site. Note that this refers to mechanical compressors and heat pumps, any device which uses energy to raise the temperature of the rejected heat.
Note on B221: John Booth (2024): Report Power Usage Effectiveness and partial PUE (PUE and pPUE) according to EN 50600-4-2 or ISO/IEC 30134-2. If partial PUE is reported the Standardised KPI should be used. Consider advocating the use of trending rather than hard targets for PUE. This should be based on kW/h consumption and a consistent IT Load. Suggestions for come from EN 50600-5-1 (5.1.3.1)
Note on B222: John Booth (2022): Report REF according to EN 50600-4-3 or ISO/IEC 30134-3. If REF is reported the Standardised KPI should be used.
Note on B223: John Booth (2024): Report IT Equipment Energy Efficiency for Servers (ITEEsv) according to EN 50600-4-4 or ISO/IEC 30134-4. If ITEEsv is reported the Standardised KPI should be used.
Note on B224: John Booth (2024): Report IT Equipment Utilization for Servers (ITEUsv) according to EN 50600-4-5 or ISO/IEC 30134-5. If ITEUsv is reported the Standardised KPI should be used.
Note on B225: John Booth:2024 Report Energy Reuse Factor (ERF) according to EN 50600-4-6 or ISO/IEC 30134-6. If CER is reported the Standardised KPI should be used.
Note on B226: John Booth: 2024 Report Cooling Efficiency Ratio (CER) according to EN 50600-4-7 or ISO/IEC 30134-7. If CER is reported the Standardised KPI should be used. Consider advocating the use of trending rather than hard targets for CER. This should be based on kW/h consumption and a consistent IT Load. Suggestions come from EN 50600-5-1 (8.1.3.1)
Note on B227: John Booth: 2024 Report Carbon Usage Effectiveness (CUE) according to ISO/IEC 30134-8. If CUE is reported the Standardised KPI should be used. Consider advocating the use of trending rather than hard targets for CuE. This should be based on kW/h consumption and a consistent IT Load.
Note on B228: John Booth: 2024 Report Water Usage Effectiveness (WUE) according to ISO/IEC 30134-9. If WUE is reported the Standardised KPI should be used. Consider advocating the use of trending rather than hard targets for WUE. This should be based on kW/h consumption and a consistent IT Load.
Note on B231: John Booth: 2024 Logging and internal reporting of the processor utilisation of the overall or grouped by service / location IT server estate. Whilst effective metrics and reporting mechanisms are still under development a basic level of reporting can be highly informative and should consider energy efficiency. Note: Server Utilisation reporting should be performed according to EN 50600-4-4 or ISO/IEC 30134-4.
Note on B232: John Booth 2021: Logging and internal reporting of the proportion of the overall or grouped by service / location network capacity utilised. Whilst effective metrics and reporting mechanisms are still under development a basic level of reporting can be highly informative and should consider energy consumption.
Note on B233: John Booth 2021: Logging and internal reporting of the proportion of the overall storage capacity and performance utilised (Grouped by service or location). Whilst effective metrics and reporting mechanisms are still under development a basic level of reporting can be highly informative and should consider energy consumption. The meaning of utilisation can vary depending on what is considered available capacity (e.g., ports, raw v. usable data storage) and what is considered used (e.g., allocation versus active usage). Ensure the definition used in these reports is clear and consistent. Note: Mixed incentives are possible here through the use of technologies such as de-duplication.
Note on B234: John Booth: Establish sensible and useful business specific metrics and potentially a business relevant efficiency dashboard to accurately reflect, highlight, manage and ideally reduce the overall energy usage required to deliver the IT services defined by specific business requirements. Note that this goes beyond Practice 9.3.3 and the metrics chosen as relevant will vary between different businesses.

## Utility Energy Measurement
< Prev | Next> | Home
Tab 5 - Utility Energy Measurement
Data Center Name / ID | Meter ID | Start Date (DD/MM/YYYY) | End Date (DD/MM/YYYY) | Electricity Consumption (kWh)
Example #1 | Electric 45389 | 2008-02-21 | 2008-03-20 | 3283686
Note on A3: Please provide a unique name or number for each data center. Make sure to use the same identifier on each tab!
Note on E3: Please enter the building's electricity consumption.

## IT Energy Measurement
< Prev |  | Home
Tab 6- IT Measurement
Data Center Name / ID | Total IT Plug Energy from UPS Meter (kWh) | Start Date (DD/MM/YYYY) | End Date (DD/MM/YYYY) | Total IT Plug Energy from PDU Meter (kWh) If Available | Start Date (DD/MM/YYYY) | End Date (DD/MM/YYYY)
Example #1 | 1824270 | 2008-02-21 | 2008-03-20 | 1806028 | 2008-02-21 | 2008-03-20
Note on A3: Please provide a unique name or number for each data center. Make sure to use the same identifier on each tab!
Note on B3: Enter the annual total IT plug energy from the output of a UPS meter.
Note on E3: Enter the annual total IT plug energy from the input of the PDU meter, if available.

## Lists
1 - Traditional Enterprise | 1 - Stand-Alone | N/A | N/A | Yes | Water-Side | Peak Shaving | N | UPS Meter | January | 1 = Direct Expansion | 0 = None | Operator | Y |  | Return
2 - On-Demand Enterprise | 2 - Enclosed in a Larger Building | Yes | Yes | No | Air-Side | Demand Response | N+1 | PDU Meter | February | 2 = Chilled Water | 1 = Direct Air Side | Colo Provider | N | I | Supply
3 - Telecom |  | No | No |  |  | Thermal Storage | 2N |  | March | 3 = Condenser | 2 = Indirect Air Side | Colo Customer | Partial | E
4 - HPCC (Scientific) | [5 empty] | Co-generation | 2N+1 |  | April | 4 = Other | 3 = Direct Water Side | Managed Service Provider in Colo |  | I & E
5 - Hosting | [8 empty] | May |  | 4 = Indirect Water Side | Managed Service Provider
6 - Internet | [8 empty] | June |  |  | Other
7 - Hybrid | [8 empty] | July
August
September
October
November
December

## Sheet2
Compatibility Report for Copy of 2021 EUCOC Reporting_Form_v13.1 IP.xls
Run on 25/12/2021 15:44
If the workbook is saved in an earlier file format or opened in an earlier version of Microsoft Excel, the listed features will not be available.
Minor loss of fidelity | # of occurrences | Version
Some cells or styles in this workbook contain formatting that is not supported by the selected file format. These formats will be converted to the closest format available. | 11 | Excel 97-2003